## version control
version number | use / purpose | date | changes made
Template CBA RIIO ED1 v1.xls | initial draft RIIO-GD1 model issued for demo purposes |  | -
Template CBA RIIO ED1 v2.xls | draft RIIO-ED1 model demonstrated during the CBA meeting held on the 19 March | 2013-03-19 | updated the model to reflect ED1 rather than GD1
Template CBA RIIO ED1 v3.xls | issued to DNOs to complete the 2 worked examples (leaking cable and QoS) | 28/03/2013 03/04/2013 | updated to reflect discussions at the CBA meeting including straight line depreciation assumption for ED1, addition of fixed parameter assumptions for non-monetary items re-issued on 3 April to correct CI/CML fixed data transpose error
Template CBA RIIO ED1 v4.xls | final version of CBA spreadsheet to take into account worked examples | 2013-04-16 | updated to reflect DNO feedback following completion of worked examples main changes include: - included baseline scenario worksheet - removed VOLL as CI/CML method of monetising loss of supply was viewed as robust method - amended the CO2 conversion factor associated with losses to take into account assumptions regarding future decarbonisation of electricity - updated fixed data parameters to 2012/13 prices

## Guidance
Guidance for CBA spreadsheet model
Tab | Instructions
Option summary | Provide a description of the stated aim / investment decision contained within this CBA analysis workbook, along with a list of options considered to meet the aim. Also include here the short list of options contained within this workbook which have been fully costed and specify which option has been adopted following CBA and included in your business plan submission.
Fixed data | Enter pre-tax WACC and prices consistent with your business plan
Baseline scenario | Enter costs and benefits associated with the baseline scenario. The baseline scenario represents status quo; that is the cost of business as usual in the absence of any investment intervention. Where business as usual is not an option i.e. an investment intervention of some kind is required DNOs should chose the option with the lowest investment to represent the baseline scenario.
Working baseline | Show any calculation used to derive the values in your baseline scenario
Option 1 | Enter costs and benefits over and above the baseline scenario i.e. the marginal or incremental costs / benefits of the option being considered. Enter capitalisation rates consistent with your business plan.
Working 1 | Show any calculation used to derive the values in your CBA
Colour code:
User populated cells
Fixed data
Summation formula
Other formula
The user should populate the light blue cells. All other cells are either fixed or auto-populated.
Enter costs / benefits in 2012/13 prices (£m).
Costs should be entered as negative values.
Benefits (i.e. avoided costs) should be entered a positive values.
Costs entered should correspond to values set out in company business plans i.e. should exclude RPEs and include ongoing efficiencies consistent with assumptions contained in your business plan submission.
Copy Option 1 worksheet & workings 1 for each CBA option and label these option 2 & workings 2 etc.
Where a 'do minimum option' exists, Option 1 should represent your 'do minimum' or 'reference scenario' e.g. do nothing, ongoing maintenance of existing asset or the option which requires the minimum investment .
Use the relevant Workings worksheet to demonstrate any calculation/information that can support the costs and benefits you have entered for each option. This is free fill and provides you with an opportunity to show additional underlying data you believe will assist Ofgem in evaluating/understanding your CBA.
Please highlight your chosen option by colouring the worksheet tab yellow.

## Option summary
Purpose of CBA: describe the stated aim of the investment decision | [9 empty] | Adopted | Total
The aim of this Cost Benefit Analysis (CBA) is to demonstrate that the proposed condition based asset replacement programme for 11kV CB GM (primary) delivers a cost effective reduction in the risk of condition based failure. This CBA specifically relates to South West. |  |  |  |  | South West |  |  |  |  | Rejected | LV SGR at Subs
[5 empty] | 11kV CB GM (primary) | [5 empty] | HV GM SWGR (secondary)
If investment is to replace an existing asset / asset class, please state the condition of the asset / asset class (HI / CI etc.) | [10 empty] | 11kV CB GM (primary)
The proposed programme targets the replacement of assets that permit the optimisation of risk reduction. The risk has been derived from the combination of: - Probability of asset failure (which correlates to Health Indices); and - Consequences of asset failure (which correlates to Criticality Index). Asset volumes has been determined where the Health Indices and Criticality Indices indicate that the optimum risk reduction can be achieved. Consequently the programme caters for assets with a range of Health Indices and Criticality Indices. | [10 empty] | 11kV CB GM (Secondary)
11kV CB PM
List below all options considered to meet the stated aim | [10 empty] | 11kV RMU
Options considered |  | Comment | [8 empty] | 11kV Switch GM
Baseline Scenario |  | No intervention | [8 empty] | 11kV Switch PM
Option 1 |  | Asset Replacement Programme | [8 empty] | 11kV Switchgear Other PM
Option 1(i) |  | Sensitivity Analysis of Option 1 - Asset Replacement Programme Delivered With 10% Increased Costs | [8 empty] | 11kV Transformer (GM)
Option 1(ii) |  | Sensitivity Analysis of Option 1 - Asset Replacement Programme Achieving 20% Lower Benefits | [8 empty] | 11kV Transformer (PM)
132kV CB ID (Air Ins)
132kV CB ID (Gas Ins)
132kV CB OD (Air Ins)
132kV CB OD (Gas Ins)
132kV Switchgear Other
132kV Transformer
33kV CB ID (Air Ins)
33kV CB ID (Gas Ins)
33kV CB OD (Air Ins)
33kV CB OD (Gas Ins)
33kV RMU
33kV Switch (GM)
List below the short list of those options which have been costed within this CBA workbook | [10 empty] | 33kV Switch (PM)
Option no. | Options considered | Decision | Comment | Spend area (from Table C1) (relevant only to adopted option) | NPVs based on payback periods | [5 empty] | 33kV Switchgear Other
[5 empty] | 16 years | 24 years | 32 years | 45 years | DNO view |  | 33kV Transformer (GM)
Baseline | No intervention | Rejected | Investment is needed to manage future risk levels, therefore this option was not chosen | [7 empty] | 33kV Transformer (PM)
1 | Asset Replacement Programme | Adopted | Forecasts for RIIO-ED1 indicate increased probability of asset failures as the condition of assets degrade resulting in increasing levels of safety, environment and network performance risks, alongside increasing repair costs. The asset replacement programme looks to address the highest risk assets. The cost of this replacement is far outweighed by the benefits of the risk avoided. | Asset Replacement | 32.4898 | 58.0537 | 79.4381 | 108.9815 |  |  | LV Board WM
1(i) | Sensitivity Analysis of Option 1 - Asset Replacement Programme Delivered With 10% Increased Costs |  |  |  | 31.5902 | 56.9002 | 78.117 | 107.4918 |  |  | LV CB
1(ii) | Sensitivity Analysis of Option 1 - Asset Replacement Programme Achieving 20% Lower Benefits |  |  |  | 24.6277 | 45.0513 | 62.3535 | 86.4958 |  |  | LV Pillar ID
LV Pillar OD
LV UGB & LV Pillar OD not at ss
66kV CB ID (Air Ins)
66kV CB OD (Air Ins)
66kV Switchgear Other
If more options are costed, please copy Option 1 and workings 1 worksheets and add detail to the short list table above. | [10 empty] | 66kV Transformer

## Fixed data
Parameters |  |  |  | Prices
[6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52
| 4.83% | enter DNO specific pre-tax WACC figure |  |  | 2012/13 prices | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067
Discount Rate <= 30 years | 3.5% |  |  | Traded carbon price (£/t 2010/11)1 |  | 6.76 | 7.1 | 7.55 | 8.03 | 8.55 | 15.26 | 21.97 | 28.68 | 35.39 | 42.1 | 48.81 | 55.52 | 62.23 | 68.94 | 75.65 | 81 | 88 | 95 | 102 | 109 | 116 | 122 | 129 | 136 | 143 | 150 | 157 | 164 | 171 | 178 | 184 | 191 | 198 | 205 | 212 | 220 | 227 | 234 | 241 | 248 | 256 | 262 | 269 | 276 | 282 | 287 | 292 | 297 | 301 | 305 | 309 | 312
Discount Rate > 30 years | 3% |  |  | traded carbon price (£/t 2012/13 prices) |  | 7.3032 | 7.6706 | 8.1567 | 8.6753 | 9.2371 | 16.4863 | 23.7356 | 30.9848 | 38.234 | 45.4832 | 52.7325 | 59.9817 | 67.2309 | 74.4802 | 81.7294 | 87.5093 | 95.0719 | 102.6344 | 110.1969 | 117.7595 | 125.322 | 131.8042 | 139.3667 | 146.9292 | 154.4918 | 162.0543 | 169.6168 | 177.1794 | 184.7419 | 192.3044 | 198.7866 | 206.3492 | 213.9117 | 221.4742 | 229.0368 | 237.6797 | 245.2422 | 252.8047 | 260.3673 | 267.9298 | 276.5727 | 283.0549 | 290.6174 | 298.1799 | 304.6621 | 310.0639 | 315.4657 | 320.8675 | 325.189 | 329.5104 | 333.8319 | 337.073
Discount rate for safety | 1.5% |  |  | Losses (£/MWh) | 48.4213
Assumed Asset Life (Years) | 45 |  |  | CI (£s per interruption) | 15.4435
|  |  |  | CML (£s per minute lost) | 0.37667
|  |  |  | Cost per fatality (£m)2 | 1.7925
|  |  |  | Cost per major injury (£m)2 | 0.027488
RPI INDICES |  |  |  | Cost per litre oil (£/litre) | 36.0814
Using yearly averages (April to March) |  |  |  | Electricity GHG conversion factor (tonnes per MWh)3 |  | 0.50285 | 0.48835 | 0.47386 | 0.45936 | 0.44487 | 0.43037 | 0.41587 | 0.40138 | 0.38688 | 0.37239 | 0.35789 | 0.3434 | 0.3289 | 0.31441 | 0.29991 | 0.28541 | 0.27092 | 0.25642 | 0.24193 | 0.22743 | 0.21294 | 0.19844 | 0.18395 | 0.16945 | 0.15496 | 0.14046 | 0.12596 | 0.11147 | 0.096973 | 0.082478 | 0.067982 | 0.053487 | 0.038991 | 0.024496 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Index |  | convert to
2012/13
Convert from | 2003/04 | 1.3409 |  | 1 https://www.gov.uk/carbon-valuation |  | 2 2017: note: 2016 to 2030 DECC's updated traded sector carbon values published Oct 2012, 2031 onwards based on DECC carbon values published Oct 2011.
| 2004/05 | 1.3004 |  | 2 http://www.hse.gov.uk/risk/theory/alarpcheck.htm |  | 2 2017: note: HSE values as at Q3 2003
| 2005/06 | 1.267 |  | 3 http://www.defra.gov.uk/publications/2012/05/30/pb13773-2012-ghg-conversion/ |  | 2 2017: note: figures taken from 2012 Guideline to Defra / DECC's GHG conversion factors for company reporting, 'new 2010' factor annex 3 table 3(c).
| 2006/07 | 1.2214
| 2007/08 | 1.173 |  |  | FALSE
| 2008/09 | 1.1392
| 2009/10 | 1.134
| 2010/11 | 1.0804
| 2011/12 | 1.0309
| 2012/13 | 1
Decarbonisation of electricity assumption:
Power sector emissions are anticipated to reduce to 10g/kWh by 2050
assume a linear decarbonisation pathway from 2009/10 until 2050
Power sector emissions reduce by 14.5 g/kWh p.a. between now and 2030.
Beyond 2050 keep emissions at 10g/kWh
g CO2e per kWh
1,000 kg = 1 tonne | 2009/10 | 589.82 | (Defra)
1,000 kWh = 1 MWh | 2010/11 | 575.3245
1 kg = 1,000g | 2011/12 | 560.829
| 2012/13 | 546.3335
| 2013/14 | 531.838
| 2014/15 | 517.3425
| 2015/16 | 502.847
| 2016/17 | 488.3515
| 2017/18 | 473.856
| 2018/19 | 459.3605
| 2019/20 | 444.865
| 2012/21 | 430.3695
| 2021/22 | 415.874
| 2022/23 | 401.3785
| 2023/24 | 386.883
| 2024/25 | 372.3875
| 2025/26 | 357.892
| 2026/27 | 343.3965
| 2027/28 | 328.901
| 2028/29 | 314.4055
| 2029/30 | 299.91
| 2030/31 | 285.4145
| 2031/32 | 270.919
| 2032/33 | 256.4235
| 2033/34 | 241.928
| 2034/35 | 227.4325
| 2035/36 | 212.937
| 2036/37 | 198.4415
| 2037/38 | 183.946
| 2038/39 | 169.4505
| 2039/40 | 154.955
| 2040/41 | 140.4595
| 2041/42 | 125.964
| 2042/43 | 111.4685
| 2043/44 | 96.973
| 2044/45 | 82.4775
| 2045/46 | 67.982
| 2046/47 | 53.4865
| 2047/48 | 38.991
| 2048/49 | 24.4955
| 2049/50 | 10
| check | 10 | assumption; power sector should reduce to 10 g CO2e/kWh
|  | 14.4955 | p.a. reduction in carbon intensity
Exclude societal benefits

## Baseline scenario
| CBA Option - Baseline Scenario | No intervention |  | South West - 11kV CB GM (primary) | [51 empty] | Total
LV SGR at Subs
HV GM SWGR (secondary)
|  |  |  | RIIO-ED1 | [7 empty] | RIIO-ED2 | [7 empty] | RIIO-ED3 | [7 empty] | RIIO-ED4 | [7 empty] | RIIO-ED5 | [7 empty] | RIIO-ED6 | [7 empty] | RIIO-ED7 |  |  |  | 11kV CB GM (primary)
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 11kV CB GM (Secondary)
|  | Calculation | Units | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 11kV CB PM
Investment | Trouble Call / faults |  | £m | -0.35418 | -0.3826 | -0.41216 | -0.44214 | -0.4781 | -0.50841 | -0.53399 | -0.55992 | -0.59134 | -0.6219 | -0.65225 | -0.68247 | -0.71108 | -0.7349 | -0.75686 | -0.77623 | -0.78902 | -0.79729 | -0.80243 | -0.80369 | -0.80441 | -0.80466 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | [7 empty] | 11kV RMU
| Please specify |  | £m | [52 empty] | 11kV Switch GM | bar: RIIO-ED1 1 to RIIO-ED6 45
| Please specify |  | £m | [52 empty] | 11kV Switch PM | bar: RIIO-ED1 1 to RIIO-ED6 45
| Please specify |  | £m | [52 empty] | 11kV Switchgear Other PM | bar: RIIO-ED1 1 to RIIO-ED6 45
| Please specify |  | £m | [52 empty] | 11kV Transformer (GM) | bar: RIIO-ED1 1 to RIIO-ED6 45
| Total investment |  | £m | -0.35418 | -0.3826 | -0.41216 | -0.44214 | -0.4781 | -0.50841 | -0.53399 | -0.55992 | -0.59134 | -0.6219 | -0.65225 | -0.68247 | -0.71108 | -0.7349 | -0.75686 | -0.77623 | -0.78902 | -0.79729 | -0.80243 | -0.80369 | -0.80441 | -0.80466 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | -0.80471 | [7 empty] | 11kV Transformer (PM)
Societal costs (£m) | Losses |  | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV CB ID (Air Ins)
| CO2e associated with losses |  | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV CB ID (Gas Ins)
| Customer interruptions (CI) |  | £m | -1.0243 | -1.108 | -1.1958 | -1.2856 | -1.3941 | -1.489 | -1.5728 | -1.6584 | -1.7632 | -1.8657 | -1.9684 | -2.0718 | -2.1726 | -2.2619 | -2.3477 | -2.4272 | -2.4825 | -2.517 | -2.5404 | -2.5487 | -2.5538 | -2.5556 | -2.5559 | -2.5559 | -2.5559 | -2.5559 | -2.5559 | -2.5559 | -2.5559 | -2.5559 | -2.5559 | -2.5559 | -2.5559 | -2.5559 | -2.5559 | -2.5559 | -2.5559 | -2.5559 | -2.5559 | -2.5559 | -2.5559 | -2.5559 | -2.5559 | -2.5559 | -2.5559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV CB OD (Air Ins)
| Customer minutes lost (CML) |  | £m | -1.864 | -2.0162 | -2.1761 | -2.3394 | -2.5368 | -2.7094 | -2.862 | -3.0177 | -3.2085 | -3.395 | -3.5818 | -3.7701 | -3.9534 | -4.116 | -4.2721 | -4.4167 | -4.5174 | -4.5801 | -4.6228 | -4.6379 | -4.6471 | -4.6503 | -4.651 | -4.651 | -4.651 | -4.651 | -4.651 | -4.651 | -4.651 | -4.651 | -4.651 | -4.651 | -4.651 | -4.651 | -4.651 | -4.651 | -4.651 | -4.651 | -4.651 | -4.651 | -4.651 | -4.651 | -4.651 | -4.651 | -4.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV CB OD (Gas Ins)
| Other GHG emissions (CO2e) i.e. not associated with losses |  | £m | -5.0224e-05 | -5.7119e-05 | -6.557e-05 | -7.4949e-05 | -8.6459e-05 | -0.00016437 | -0.00024888 | -0.00034108 | -0.00044508 | -0.00055746 | -0.00067855 | -0.00080833 | -0.00094473 | -0.0010823 | -0.0012237 | -0.0013442 | -0.0014848 | -0.0016198 | -0.0017504 | -0.0018735 | -0.0019957 | -0.0020996 | -0.0022202 | -0.0023407 | -0.0024611 | -0.0025816 | -0.0027021 | -0.0028226 | -0.002943 | -0.0030635 | -0.0031668 | -0.0032872 | -0.0034077 | -0.0035282 | -0.0036487 | -0.0037863 | -0.0039068 | -0.0040273 | -0.0041478 | -0.0042682 | -0.0044059 | -0.0045092 | -0.0046297 | -0.0047501 | -0.0048534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV Switchgear Other
| Fatality |  | £m | -0.028735 | -0.0311 | -0.033565 | -0.036066 | -0.039079 | -0.041576 | -0.043633 | -0.04572 | -0.048272 | -0.050784 | -0.053284 | -0.055766 | -0.058013 | -0.059875 | -0.061615 | -0.063101 | -0.064053 | -0.064648 | -0.065019 | -0.065114 | -0.065172 | -0.065196 | -0.065204 | -0.065204 | -0.065204 | -0.065204 | -0.065204 | -0.065204 | -0.065204 | -0.065204 | -0.065204 | -0.065204 | -0.065204 | -0.065204 | -0.065204 | -0.065204 | -0.065204 | -0.065204 | -0.065204 | -0.065204 | -0.065204 | -0.065204 | -0.065204 | -0.065204 | -0.065204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV Transformer
| Major injury |  | £m | -0.00097598 | -0.0010563 | -0.00114 | -0.001225 | -0.0013273 | -0.0014121 | -0.001482 | -0.0015529 | -0.0016396 | -0.0017249 | -0.0018098 | -0.001894 | -0.0019704 | -0.0020336 | -0.0020927 | -0.0021432 | -0.0021755 | -0.0021957 | -0.0022083 | -0.0022115 | -0.0022135 | -0.0022143 | -0.0022145 | -0.0022145 | -0.0022145 | -0.0022145 | -0.0022145 | -0.0022145 | -0.0022145 | -0.0022145 | -0.0022145 | -0.0022145 | -0.0022145 | -0.0022145 | -0.0022145 | -0.0022145 | -0.0022145 | -0.0022145 | -0.0022145 | -0.0022145 | -0.0022145 | -0.0022145 | -0.0022145 | -0.0022145 | -0.0022145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33kV CB ID (Air Ins)
| Oil leakage |  | £m | -0.0038052 | -0.0041204 | -0.0044482 | -0.0047807 | -0.0051795 | -0.0055171 | -0.0058024 | -0.0060917 | -0.0064421 | -0.0067828 | -0.0071212 | -0.007458 | -0.0077767 | -0.0080417 | -0.008286 | -0.0085012 | -0.0086431 | -0.0087344 | -0.008791 | -0.008805 | -0.0088131 | -0.0088159 | -0.0088165 | -0.0088165 | -0.0088165 | -0.0088165 | -0.0088165 | -0.0088165 | -0.0088165 | -0.0088165 | -0.0088165 | -0.0088165 | -0.0088165 | -0.0088165 | -0.0088165 | -0.0088165 | -0.0088165 | -0.0088165 | -0.0088165 | -0.0088165 | -0.0088165 | -0.0088165 | -0.0088165 | -0.0088165 | -0.0088165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33kV CB ID (Gas Ins)
| Other 1 (specify) |  | £m | [52 empty] | 33kV CB OD (Air Ins)
| Other 2 (specify) |  | £m | [52 empty] | 33kV CB OD (Gas Ins)
| Other 3 (specify) |  | £m | [52 empty] | 33kV RMU
| Total societal net benefits |  | £m | -2.9219 | -3.1606 | -3.4111 | -3.6672 | -3.9766 | -4.2471 | -4.4859 | -4.7298 | -5.0285 | -5.3205 | -5.6131 | -5.9078 | -6.1947 | -6.4489 | -6.693 | -6.919 | -7.0763 | -7.1743 | -7.241 | -7.2646 | -7.2791 | -7.2842 | -7.2854 | -7.2855 | -7.2856 | -7.2858 | -7.2859 | -7.286 | -7.2861 | -7.2862 | -7.2863 | -7.2865 | -7.2866 | -7.2867 | -7.2868 | -7.287 | -7.2871 | -7.2872 | -7.2873 | -7.2874 | -7.2876 | -7.2877 | -7.2878 | -7.2879 | -7.288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33kV Switch (GM)
33kV Switch (PM)
33kV Switchgear Other
| Non-DNO (eg societal) benefits | [54 empty] | 33kV Transformer (GM)
33kV Transformer (PM)
Societal costs | Reduced losses |  | MWh | [52 empty] | LV Board WM
| Reduced emissions associated with losses |  | tCO2e | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LV CB
| Reduced number of customers interrupted |  | no. | -66327.8855 | -71746.5744 | -77433.5679 | -83245.6371 | -90270.4622 | -96413.5806 | -101840.2137 | -107382.0654 | -114171.7154 | -120807.9536 | -127455.9644 | -134154.6716 | -140679.4003 | -146463.1202 | -152019.1102 | -157165.7828 | -160748.2665 | -162979.9441 | -164497.6904 | -165035.4347 | -165363.7962 | -165477.972 | -165502.3182 | -165502.3182 | -165502.3182 | -165502.3182 | -165502.3182 | -165502.3182 | -165502.3182 | -165502.3182 | -165502.3182 | -165502.3182 | -165502.3182 | -165502.3182 | -165502.3182 | -165502.3182 | -165502.3182 | -165502.3182 | -165502.3182 | -165502.3182 | -165502.3182 | -165502.3182 | -165502.3182 | -165502.3182 | -165502.3182 | [7 empty] | LV Pillar ID
| Reduced customer minutes lost |  | Mins | -4948537.1413 | -5352810.0016 | -5777100.0868 | -6210721.583 | -6734823.0766 | -7193142.7039 | -7598007.4399 | -8011468.3424 | -8518023.5659 | -9013133.3086 | -9509121.0464 | -10008891.0355 | -10495680.9739 | -10927186.4666 | -11341701.2972 | -11725678.1705 | -11992955.9043 | -12159454.3796 | -12272688.8222 | -12312808.4282 | -12337306.5146 | -12345824.8253 | -12347641.2248 | -12347641.2248 | -12347641.2248 | -12347641.2248 | -12347641.2248 | -12347641.2248 | -12347641.2248 | -12347641.2248 | -12347641.2248 | -12347641.2248 | -12347641.2248 | -12347641.2248 | -12347641.2248 | -12347641.2248 | -12347641.2248 | -12347641.2248 | -12347641.2248 | -12347641.2248 | -12347641.2248 | -12347641.2248 | -12347641.2248 | -12347641.2248 | -12347641.2248 | [7 empty] | LV Pillar OD
| Reduced emissions (not associated with losses)1 |  | tCO2e | -6.8769 | -7.4465 | -8.0387 | -8.6393 | -9.36 | -9.9698 | -10.4853 | -11.0079 | -11.641 | -12.2564 | -12.8678 | -13.4762 | -14.052 | -14.5308 | -14.9721 | -15.361 | -15.6172 | -15.7823 | -15.8845 | -15.9098 | -15.9244 | -15.9294 | -15.9305 | -15.9305 | -15.9305 | -15.9305 | -15.9305 | -15.9305 | -15.9305 | -15.9305 | -15.9305 | -15.9305 | -15.9305 | -15.9305 | -15.9305 | -15.9305 | -15.9305 | -15.9305 | -15.9305 | -15.9305 | -15.9305 | -15.9305 | -15.9305 | -15.9305 | -15.9305 | [7 empty] | LV UGB & LV Pillar OD not at ss
| Reduced probability of fatality2 |  | % | -0.016031 | -0.01735 | -0.018726 | -0.020121 | -0.021802 | -0.023195 | -0.024343 | -0.025507 | -0.026931 | -0.028332 | -0.029727 | -0.031111 | -0.032365 | -0.033403 | -0.034374 | -0.035204 | -0.035735 | -0.036066 | -0.036273 | -0.036326 | -0.036359 | -0.036372 | -0.036376 | -0.036376 | -0.036376 | -0.036376 | -0.036376 | -0.036376 | -0.036376 | -0.036376 | -0.036376 | -0.036376 | -0.036376 | -0.036376 | -0.036376 | -0.036376 | -0.036376 | -0.036376 | -0.036376 | -0.036376 | -0.036376 | -0.036376 | -0.036376 | -0.036376 | -0.036376 | [7 empty] | 66kV CB ID (Air Ins)
| Reduced probability of major injury2 |  | % | -0.035506 | -0.038428 | -0.041475 | -0.044565 | -0.048288 | -0.051372 | -0.053915 | -0.056493 | -0.059647 | -0.06275 | -0.065839 | -0.068905 | -0.071681 | -0.073981 | -0.076132 | -0.077968 | -0.079144 | -0.079878 | -0.080337 | -0.080454 | -0.080525 | -0.080555 | -0.080564 | -0.080564 | -0.080564 | -0.080564 | -0.080564 | -0.080564 | -0.080564 | -0.080564 | -0.080564 | -0.080564 | -0.080564 | -0.080564 | -0.080564 | -0.080564 | -0.080564 | -0.080564 | -0.080564 | -0.080564 | -0.080564 | -0.080564 | -0.080564 | -0.080564 | -0.080564 | [7 empty] | 66kV CB OD (Air Ins)
| Reduced oil leakage |  | Litres | -105.4606 | -114.1979 | -123.2828 | -132.4966 | -143.5507 | -152.9068 | -160.8149 | -168.832 | -178.5439 | -187.985 | -197.3643 | -206.6991 | -215.532 | -222.8778 | -229.6465 | -235.6126 | -239.543 | -242.0758 | -243.6436 | -244.0317 | -244.2557 | -244.3327 | -244.3491 | -244.3491 | -244.3491 | -244.3491 | -244.3491 | -244.3491 | -244.3491 | -244.3491 | -244.3491 | -244.3491 | -244.3491 | -244.3491 | -244.3491 | -244.3491 | -244.3491 | -244.3491 | -244.3491 | -244.3491 | -244.3491 | -244.3491 | -244.3491 | -244.3491 | -244.3491 | [7 empty] | 66kV Switchgear Other
66kV Transformer
1 | Includes all GHG not associated with losses e.g. SF6 converted to tCO2e using Defra conversion factors
http://www.defra.gov.uk/publications/2012/05/30/pb13773-2012-ghg-conversion/
Where losses are entered in terms of MWh, the CO2e associated with those losses will be calculated based on an assumed GHG conversion factor. The tCO2e are monetised using DECC traded carbon values.
All other GHG emissions not associated with losses should be entered in row 33 to avoid double counting.
2 | http://www.hse.gov.uk/risk/theory/alarpcheck.htm
Please specify
Total investment
Connections
Diversions
Reinforcement
ESQCR
Asset Replacement
Refurbishment
Civil Works
Operational IT & Telecoms
Legal & Safety
QoS
High Value Projects
Flooding
BT21CN
Technical losses and other environmental
High impact Low Probability (HILP)
Critical National Infrastructure
Black Start
Rising Mains and Laterals
Undergrounding Within/ Outside designated areas
Worst Served Customers
Trouble Call / faults
ONIs
Inspections & Maintenance
Tree Cutting
NOC's Other
Network Design & Engineering
Project Management
Engineering Mgt & Clerical Support
System Mapping - Cartographical
Control Centre
Call Centre
Stores
Operational Training
Vehicles & Transport
Atypicals Non Sev Weather
Smart Meters
Network Policy
HR & Non-operational Training
Finance & Regulation
CEO
IT & Telecoms
Property Mgt
Non Op Capex

## Workings baseline
Workings / assumptions used for costing Baseline
Use this sheet to provide details of assumptions and calculation methodology used in CBA model
Investment | Trouble Call / faults | Forecast repair costs with no intervention, for those assets that will be replaced during RIIO-ED1. Forecast costs estimated using probability of failure and weighted repair/replacement costs derived from CBRM asset health/ consequence models.
Please specify
Please specify
Please specify
Please specify
Total investment
Societal costs | Reduced losses
Reduced emissions associated with losses
| Reduced number of customers interrupted | Forecast customers interrupted associated with condition based failure of those assets that will be replaced during RIIO-ED1, assuming no intervention. Forecast number of customers interrupted estimated using probability of failure and network performance consequences derived from CBRM asset health/ consequence models.
| Reduced customer minutes lost | Forecast customer minutes lost associated with condition based failure of those assets that will be replaced during RIIO-ED1, assuming no intervention. Forecast number of customer minutes lost estimated using probability of failure and network performance consequences derived from CBRM asset health/ consequence models.
| Reduced emissions (not associated with losses)1 | Forecast SF6 emissions from those assets that will be replaced during RIIO-ED1, assuming no intervention. Forecast SF6 emissions estimated using probability of failure and consequences ( volume of SF6 lost per condition based failure) derived from CBRM asset health/ consequence models.
| Reduced probability of fatality2 | Forecast probability of fatality associated with condition based failure of those assets that will be replaced during RIIO-ED1, assuming no intervention. This is derived by combining the probability of condition based asset failure, with the probability that a failure would result in a fatality - as derived from CBRM asset health/ consequence models.
| Reduced probability of major injury2 | Forecast probability of major injury associated with condition based failure of those assets that will be replaced during RIIO-ED1, assuming no intervention. This is derived by combining the probability of condition based asset failure, with the probability that a major injury would result in a fatality - as derived from CBRM asset health/ consequence models.
| Reduced oil leakage | Forecast oil leakage from those assets that will be replaced during RIIO-ED1, assuming no intervention. Forecast oil leakage estimated using probability of failure and consequences ( volume of oil lost per condition based failure) derived from CBRM asset health/ consequence models.

## Option 1
| CBA Option 1 - Option 1 | Asset Replacement Programme |  | South West - 11kV CB GM (primary)
| Term (years from first out flow) | NPV (£m)
| 16 | 32.4898
| 24 | 58.0537
| 32 | 79.4381
| 45 | 108.9815
| first year of investment out flow | 1
|  |  |  | RIIO-ED1 | [7 empty] | RIIO-ED2 | [7 empty] | RIIO-ED3 | [7 empty] | RIIO-ED4 | [7 empty] | RIIO-ED5 | [7 empty] | RIIO-ED6 | [7 empty] | RIIO-ED7
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52
|  | Calculation | Units | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067
Investment | Asset Replacement |  | £m | RIIO-ED1 1: -1.9091; RIIO-ED1 2: -1.8888; RIIO-ED1 3: -1.8683; RIIO-ED1 4: -1.8711; RIIO-ED1 5: -1.85; RIIO-ED1 6: -1.8294; RIIO-ED1 7: -1.8093; RIIO-ED1 8: -1.7886
| Please specify |  | £m | bar: RIIO-ED1 1 to RIIO-ED6 45
| Please specify |  | £m | bar: RIIO-ED1 1 to RIIO-ED6 45
| Please specify |  | £m | bar: RIIO-ED1 1 to RIIO-ED6 45
| Please specify |  | £m | bar: RIIO-ED1 1 to RIIO-ED6 45
| Total investment |  | £m | -1.9091 | -1.8888 | -1.8683 | -1.8711 | -1.85 | -1.8294 | -1.8093 | -1.7886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avoided DNO costs | Trouble Call / faults |  | £m | 0 | 0.064888 | 0.1387 | 0.20502 | 0.26256 | 0.31995 | 0.37437 | 0.43494 | 0.50111 | 0.53166 | 0.56202 | 0.59224 | 0.62085 | 0.64466 | 0.66663 | 0.686 | 0.69879 | 0.70706 | 0.7122 | 0.71345 | 0.71418 | 0.71442 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448
| Please specify |  | £m
| Please specify |  | £m
| Please specify |  | £m
| Please specify |  | £m
| Please specify |  | £m
| Total avoided DNO costs |  | £m | 0 | 0.064888 | 0.1387 | 0.20502 | 0.26256 | 0.31995 | 0.37437 | 0.43494 | 0.50111 | 0.53166 | 0.56202 | 0.59224 | 0.62085 | 0.64466 | 0.66663 | 0.686 | 0.69879 | 0.70706 | 0.7122 | 0.71345 | 0.71418 | 0.71442 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total DNO net benefits before capitalisation | (1) = investment + DNO benefits | £m | -1.9091 | -1.8239 | -1.7296 | -1.6661 | -1.5874 | -1.5094 | -1.4349 | -1.3537 | 0.50111 | 0.53166 | 0.56202 | 0.59224 | 0.62085 | 0.64466 | 0.66663 | 0.686 | 0.69879 | 0.70706 | 0.7122 | 0.71345 | 0.71418 | 0.71442 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capitalisation rates | (2) | % | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80%
| Capitalised investment | (3)=(1)x(2) | £m | -1.5273 | -1.4591 | -1.3837 | -1.3329 | -1.27 | -1.2076 | -1.1479 | -1.0829 | 0.40089 | 0.42533 | 0.44962 | 0.47379 | 0.49668 | 0.51573 | 0.5333 | 0.5488 | 0.55903 | 0.56565 | 0.56976 | 0.57076 | 0.57134 | 0.57154 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158
| Investment to be expensed | (4)=(1)-(3) | £m | -0.38182 | -0.36478 | -0.34592 | -0.33322 | -0.31749 | -0.30189 | -0.28699 | -0.27073 | 0.10022 | 0.10633 | 0.1124 | 0.11845 | 0.12417 | 0.12893 | 0.13333 | 0.1372 | 0.13976 | 0.14141 | 0.14244 | 0.14269 | 0.14284 | 0.14288 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429
| 2016 Depreciation | (5)2016=(3)2016*Dep_ratet | £m |  | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394
| 2017 Depreciation | (5)2017=(3)2017*Dep_ratet | £m |  |  | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425
| 2018 Depreciation | (5)2018=(3)2018*Dep_ratet | £m |  |  |  | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748
| 2019 Depreciation | (5)2019=(3)2019*Dep_ratet | £m |  |  |  |  | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619
| 2020 Depreciation | (5)2020=(3)2020*Dep_ratet | £m | [5 empty] | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221
| 2021 Depreciation | (5)2021=(3)2021*Dep_ratet | £m | [6 empty] | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835
| 2022 Depreciation | (5)2022=(3)2022*Dep_ratet | £m | [7 empty] | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551
| 2023 Depreciation | (5)2023=(3)2023*Dep_ratet | £m | [8 empty] | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065
| 2024 Depreciation | (5)2024=(3)2024*Dep_ratet | £m | [9 empty] | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086
| 2025 Depreciation | (5)2025=(3)2025*Dep_ratet | £m | [10 empty] | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518
| 2026 Depreciation | (5)2026=(3)2026*Dep_ratet | £m | [11 empty] | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915
| 2027 Depreciation | (5)2027=(3)2027*Dep_ratet | £m | [12 empty] | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529
| 2028 Depreciation | (5)2028=(3)2028*Dep_ratet | £m | [13 empty] | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037
| 2029 Depreciation | (5)2029=(3)2029*Dep_ratet | £m | [14 empty] | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461
| 2030 Depreciation | (5)2030=(3)2030*Dep_ratet | £m | [15 empty] | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851
| 2031 Depreciation | (5)2031=(3)2031*Dep_ratet | £m | [16 empty] | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196
| 2032 Depreciation | (5)2032=(3)2032*Dep_ratet | £m | [17 empty] | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423
| 2033 Depreciation | (5)2033=(3)2033*Dep_ratet | £m | [18 empty] | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257
| 2034 Depreciation | (5)2034=(3)2034*Dep_ratet | £m | [19 empty] | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661
| 2035 Depreciation | (5)2035=(3)2035*Dep_ratet | £m | [20 empty] | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684
| 2036 Depreciation | (5)2036=(3)2036*Dep_ratet | £m | RIIO-ED3 22: 0.012696; RIIO-ED3 23: 0.012696; RIIO-ED3 24: 0.012696; RIIO-ED4 25: 0.012696; RIIO-ED4 26: 0.012696; RIIO-ED4 27: 0.012696; RIIO-ED4 28: 0.012696; RIIO-ED4 29: 0.012696; RIIO-ED4 30: 0.012696; RIIO-ED4 31: 0.012696; RIIO-ED4 32: 0.012696; RIIO-ED5 33: 0.012696; RIIO-ED5 34: 0.012696; RIIO-ED5 35: 0.012696; RIIO-ED5 36: 0.012696; RIIO-ED5 37: 0.012696; RIIO-ED5 38: 0.012696; RIIO-ED5 39: 0.012696; RIIO-ED5 40: 0.012696; RIIO-ED6 41: 0.012696; RIIO-ED6 42: 0.012696; RIIO-ED6 43: 0.012696; RIIO-ED6 44: 0.012696; RIIO-ED6 45: 0.012696; RIIO-ED6 46: 0.012696; RIIO-ED6 47: 0.012696; RIIO-ED6 48: 0.012696; RIIO-ED7 49: 0.012696; RIIO-ED7 50: 0.012696; RIIO-ED7 51: 0.012696; RIIO-ED7 52: 0.012696
| 2037 Depreciation | (5)2037=(3)2037*Dep_ratet | £m | RIIO-ED3 23: 0.012701; RIIO-ED3 24: 0.012701; RIIO-ED4 25: 0.012701; RIIO-ED4 26: 0.012701; RIIO-ED4 27: 0.012701; RIIO-ED4 28: 0.012701; RIIO-ED4 29: 0.012701; RIIO-ED4 30: 0.012701; RIIO-ED4 31: 0.012701; RIIO-ED4 32: 0.012701; RIIO-ED5 33: 0.012701; RIIO-ED5 34: 0.012701; RIIO-ED5 35: 0.012701; RIIO-ED5 36: 0.012701; RIIO-ED5 37: 0.012701; RIIO-ED5 38: 0.012701; RIIO-ED5 39: 0.012701; RIIO-ED5 40: 0.012701; RIIO-ED6 41: 0.012701; RIIO-ED6 42: 0.012701; RIIO-ED6 43: 0.012701; RIIO-ED6 44: 0.012701; RIIO-ED6 45: 0.012701; RIIO-ED6 46: 0.012701; RIIO-ED6 47: 0.012701; RIIO-ED6 48: 0.012701; RIIO-ED7 49: 0.012701; RIIO-ED7 50: 0.012701; RIIO-ED7 51: 0.012701; RIIO-ED7 52: 0.012701
| 2038 Depreciation | (5)2038=(3)2038*Dep_ratet | £m | RIIO-ED3 24: 0.012702; RIIO-ED4 25: 0.012702; RIIO-ED4 26: 0.012702; RIIO-ED4 27: 0.012702; RIIO-ED4 28: 0.012702; RIIO-ED4 29: 0.012702; RIIO-ED4 30: 0.012702; RIIO-ED4 31: 0.012702; RIIO-ED4 32: 0.012702; RIIO-ED5 33: 0.012702; RIIO-ED5 34: 0.012702; RIIO-ED5 35: 0.012702; RIIO-ED5 36: 0.012702; RIIO-ED5 37: 0.012702; RIIO-ED5 38: 0.012702; RIIO-ED5 39: 0.012702; RIIO-ED5 40: 0.012702; RIIO-ED6 41: 0.012702; RIIO-ED6 42: 0.012702; RIIO-ED6 43: 0.012702; RIIO-ED6 44: 0.012702; RIIO-ED6 45: 0.012702; RIIO-ED6 46: 0.012702; RIIO-ED6 47: 0.012702; RIIO-ED6 48: 0.012702; RIIO-ED7 49: 0.012702; RIIO-ED7 50: 0.012702; RIIO-ED7 51: 0.012702; RIIO-ED7 52: 0.012702
| 2039 Depreciation | (5)2039=(3)2039*Dep_ratet | £m | RIIO-ED4 25: 0.012702; RIIO-ED4 26: 0.012702; RIIO-ED4 27: 0.012702; RIIO-ED4 28: 0.012702; RIIO-ED4 29: 0.012702; RIIO-ED4 30: 0.012702; RIIO-ED4 31: 0.012702; RIIO-ED4 32: 0.012702; RIIO-ED5 33: 0.012702; RIIO-ED5 34: 0.012702; RIIO-ED5 35: 0.012702; RIIO-ED5 36: 0.012702; RIIO-ED5 37: 0.012702; RIIO-ED5 38: 0.012702; RIIO-ED5 39: 0.012702; RIIO-ED5 40: 0.012702; RIIO-ED6 41: 0.012702; RIIO-ED6 42: 0.012702; RIIO-ED6 43: 0.012702; RIIO-ED6 44: 0.012702; RIIO-ED6 45: 0.012702; RIIO-ED6 46: 0.012702; RIIO-ED6 47: 0.012702; RIIO-ED6 48: 0.012702; RIIO-ED7 49: 0.012702; RIIO-ED7 50: 0.012702; RIIO-ED7 51: 0.012702; RIIO-ED7 52: 0.012702
| 2040 Depreciation | (5)2040=(3)2040*Dep_ratet | £m | RIIO-ED4 26: 0.012702; RIIO-ED4 27: 0.012702; RIIO-ED4 28: 0.012702; RIIO-ED4 29: 0.012702; RIIO-ED4 30: 0.012702; RIIO-ED4 31: 0.012702; RIIO-ED4 32: 0.012702; RIIO-ED5 33: 0.012702; RIIO-ED5 34: 0.012702; RIIO-ED5 35: 0.012702; RIIO-ED5 36: 0.012702; RIIO-ED5 37: 0.012702; RIIO-ED5 38: 0.012702; RIIO-ED5 39: 0.012702; RIIO-ED5 40: 0.012702; RIIO-ED6 41: 0.012702; RIIO-ED6 42: 0.012702; RIIO-ED6 43: 0.012702; RIIO-ED6 44: 0.012702; RIIO-ED6 45: 0.012702; RIIO-ED6 46: 0.012702; RIIO-ED6 47: 0.012702; RIIO-ED6 48: 0.012702; RIIO-ED7 49: 0.012702; RIIO-ED7 50: 0.012702; RIIO-ED7 51: 0.012702; RIIO-ED7 52: 0.012702
| 2041 Depreciation | (5)2041=(3)2041*Dep_ratet | £m | RIIO-ED4 27: 0.012702; RIIO-ED4 28: 0.012702; RIIO-ED4 29: 0.012702; RIIO-ED4 30: 0.012702; RIIO-ED4 31: 0.012702; RIIO-ED4 32: 0.012702; RIIO-ED5 33: 0.012702; RIIO-ED5 34: 0.012702; RIIO-ED5 35: 0.012702; RIIO-ED5 36: 0.012702; RIIO-ED5 37: 0.012702; RIIO-ED5 38: 0.012702; RIIO-ED5 39: 0.012702; RIIO-ED5 40: 0.012702; RIIO-ED6 41: 0.012702; RIIO-ED6 42: 0.012702; RIIO-ED6 43: 0.012702; RIIO-ED6 44: 0.012702; RIIO-ED6 45: 0.012702; RIIO-ED6 46: 0.012702; RIIO-ED6 47: 0.012702; RIIO-ED6 48: 0.012702; RIIO-ED7 49: 0.012702; RIIO-ED7 50: 0.012702; RIIO-ED7 51: 0.012702; RIIO-ED7 52: 0.012702
| 2042 Depreciation | (5)2042=(3)2042*Dep_ratet | £m | RIIO-ED4 28: 0.012702; RIIO-ED4 29: 0.012702; RIIO-ED4 30: 0.012702; RIIO-ED4 31: 0.012702; RIIO-ED4 32: 0.012702; RIIO-ED5 33: 0.012702; RIIO-ED5 34: 0.012702; RIIO-ED5 35: 0.012702; RIIO-ED5 36: 0.012702; RIIO-ED5 37: 0.012702; RIIO-ED5 38: 0.012702; RIIO-ED5 39: 0.012702; RIIO-ED5 40: 0.012702; RIIO-ED6 41: 0.012702; RIIO-ED6 42: 0.012702; RIIO-ED6 43: 0.012702; RIIO-ED6 44: 0.012702; RIIO-ED6 45: 0.012702; RIIO-ED6 46: 0.012702; RIIO-ED6 47: 0.012702; RIIO-ED6 48: 0.012702; RIIO-ED7 49: 0.012702; RIIO-ED7 50: 0.012702; RIIO-ED7 51: 0.012702; RIIO-ED7 52: 0.012702
| 2043 Depreciation | (5)2043=(3)2043*Dep_ratet | £m | RIIO-ED4 29: 0.012702; RIIO-ED4 30: 0.012702; RIIO-ED4 31: 0.012702; RIIO-ED4 32: 0.012702; RIIO-ED5 33: 0.012702; RIIO-ED5 34: 0.012702; RIIO-ED5 35: 0.012702; RIIO-ED5 36: 0.012702; RIIO-ED5 37: 0.012702; RIIO-ED5 38: 0.012702; RIIO-ED5 39: 0.012702; RIIO-ED5 40: 0.012702; RIIO-ED6 41: 0.012702; RIIO-ED6 42: 0.012702; RIIO-ED6 43: 0.012702; RIIO-ED6 44: 0.012702; RIIO-ED6 45: 0.012702; RIIO-ED6 46: 0.012702; RIIO-ED6 47: 0.012702; RIIO-ED6 48: 0.012702; RIIO-ED7 49: 0.012702; RIIO-ED7 50: 0.012702; RIIO-ED7 51: 0.012702; RIIO-ED7 52: 0.012702
| 2044 Depreciation | (5)2044=(3)2044*Dep_ratet | £m | RIIO-ED4 30: 0.012702; RIIO-ED4 31: 0.012702; RIIO-ED4 32: 0.012702; RIIO-ED5 33: 0.012702; RIIO-ED5 34: 0.012702; RIIO-ED5 35: 0.012702; RIIO-ED5 36: 0.012702; RIIO-ED5 37: 0.012702; RIIO-ED5 38: 0.012702; RIIO-ED5 39: 0.012702; RIIO-ED5 40: 0.012702; RIIO-ED6 41: 0.012702; RIIO-ED6 42: 0.012702; RIIO-ED6 43: 0.012702; RIIO-ED6 44: 0.012702; RIIO-ED6 45: 0.012702; RIIO-ED6 46: 0.012702; RIIO-ED6 47: 0.012702; RIIO-ED6 48: 0.012702; RIIO-ED7 49: 0.012702; RIIO-ED7 50: 0.012702; RIIO-ED7 51: 0.012702; RIIO-ED7 52: 0.012702
| 2045 Depreciation | (5)2045=(3)2045*Dep_ratet | £m | RIIO-ED4 31: 0.012702; RIIO-ED4 32: 0.012702; RIIO-ED5 33: 0.012702; RIIO-ED5 34: 0.012702; RIIO-ED5 35: 0.012702; RIIO-ED5 36: 0.012702; RIIO-ED5 37: 0.012702; RIIO-ED5 38: 0.012702; RIIO-ED5 39: 0.012702; RIIO-ED5 40: 0.012702; RIIO-ED6 41: 0.012702; RIIO-ED6 42: 0.012702; RIIO-ED6 43: 0.012702; RIIO-ED6 44: 0.012702; RIIO-ED6 45: 0.012702; RIIO-ED6 46: 0.012702; RIIO-ED6 47: 0.012702; RIIO-ED6 48: 0.012702; RIIO-ED7 49: 0.012702; RIIO-ED7 50: 0.012702; RIIO-ED7 51: 0.012702; RIIO-ED7 52: 0.012702
| Depreciation | (5)=∑(5)t | £m | 0 | -0.03394 | -0.066365 | -0.097113 | -0.12673 | -0.15495 | -0.18179 | -0.2073 | -0.23136 | -0.22245 | -0.213 | -0.20301 | -0.19248 | -0.18145 | -0.16998 | -0.15813 | -0.14594 | -0.13351 | -0.12094 | -0.10828 | -0.0956 | -0.082903 | -0.070203 | -0.057501 | -0.044799 | -0.032097 | -0.019395 | -0.0066936 | 0.0060082 | 0.01871 | 0.031412 | 0.031412 | 0.031412 | 0.031412 | 0.031412 | 0.031412 | 0.031412 | 0.031412 | 0.031412 | 0.031412 | 0.031412 | 0.031412 | 0.031412 | 0.031412 | 0.031412 | 0.031412 | 0.065351 | 0.097776 | 0.12852 | 0.15814 | 0.18637 | 0.2132
| Opening RAV balance | (6op)t=(6cl)t-1 | £m | 0 | -1.5273 | -2.9525 | -4.2698 | -5.5055 | -6.6488 | -7.7014 | -8.6675 | -9.5431 | -8.9109 | -8.2631 | -7.6005 | -6.9237 | -6.2345 | -5.5374 | -4.8341 | -4.1271 | -3.4222 | -2.723 | -2.0323 | -1.3533 | -0.68631 | -0.031869 | 0.60991 | 1.239 | 1.8554 | 2.4591 | 3.05 | 3.6283 | 4.1939 | 4.7468 | 5.2869 | 5.8271 | 6.3673 | 6.9074 | 7.4476 | 7.9878 | 8.5279 | 9.0681 | 9.6083 | 10.1484 | 10.6886 | 11.2288 | 11.769 | 12.3091 | 12.8493 | 12.8179 | 12.7525 | 12.6548 | 12.5262 | 12.3681 | 12.1817
| Closing RAV balance | (6cl)=(3)-(5)+(6op) | £m | -1.5273 | -2.9525 | -4.2698 | -5.5055 | -6.6488 | -7.7014 | -8.6675 | -9.5431 | -8.9109 | -8.2631 | -7.6005 | -6.9237 | -6.2345 | -5.5374 | -4.8341 | -4.1271 | -3.4222 | -2.723 | -2.0323 | -1.3533 | -0.68631 | -0.031869 | 0.60991 | 1.239 | 1.8554 | 2.4591 | 3.05 | 3.6283 | 4.1939 | 4.7468 | 5.2869 | 5.8271 | 6.3673 | 6.9074 | 7.4476 | 7.9878 | 8.5279 | 9.0681 | 9.6083 | 10.1484 | 10.6886 | 11.2288 | 11.769 | 12.3091 | 12.8493 | 12.8179 | 12.7525 | 12.6548 | 12.5262 | 12.3681 | 12.1817 | 11.9685
| Cost of Capital | (6)=avg[(6cl),(6op)]xWACC | £m | -0.036884 | -0.10819 | -0.17442 | -0.23607 | -0.29353 | -0.34656 | -0.39531 | -0.43979 | -0.44566 | -0.41475 | -0.38311 | -0.35076 | -0.31777 | -0.28429 | -0.25047 | -0.21641 | -0.18232 | -0.14841 | -0.11484 | -0.081761 | -0.049255 | -0.017344 | 0.01396 | 0.044651 | 0.074729 | 0.10419 | 0.13304 | 0.16128 | 0.18891 | 0.21592 | 0.24231 | 0.2684 | 0.29449 | 0.32058 | 0.34667 | 0.37276 | 0.39885 | 0.42494 | 0.45103 | 0.47712 | 0.50321 | 0.52931 | 0.5554 | 0.58149 | 0.60758 | 0.61986 | 0.61753 | 0.61359 | 0.60812 | 0.6012 | 0.59288 | 0.58323
| Total Net DNO benefits | (7)=(4)+(5)+(6) | £m | -0.4187 | -0.50691 | -0.5867 | -0.6664 | -0.73775 | -0.8034 | -0.86408 | -0.91782 | -0.57681 | -0.53087 | -0.4837 | -0.43532 | -0.38608 | -0.3368 | -0.28713 | -0.23735 | -0.1885 | -0.14051 | -0.093345 | -0.047354 | -0.0020204 | 0.042637 | 0.086652 | 0.13005 | 0.17283 | 0.21499 | 0.25654 | 0.29748 | 0.33781 | 0.37752 | 0.41662 | 0.44271 | 0.4688 | 0.49489 | 0.52098 | 0.54707 | 0.57316 | 0.59925 | 0.62534 | 0.65143 | 0.67752 | 0.70361 | 0.7297 | 0.75579 | 0.78188 | 0.65127 | 0.68288 | 0.71136 | 0.73665 | 0.75934 | 0.77924 | 0.79643
Societal benefits (£m) i.e. costs avoided | Losses |  | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CO2e associated with losses |  | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer interruptions (CI) |  | £m | 0 | 0.19785 | 0.37362 | 0.53707 | 0.75245 | 0.93829 | 1.1067 | 1.28 | 1.5007 | 1.6032 | 1.7059 | 1.8093 | 1.9101 | 1.9994 | 2.0852 | 2.1647 | 2.22 | 2.2545 | 2.2779 | 2.2862 | 2.2913 | 2.2931 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer minutes lost (CML) |  | £m | 0 | 0.36003 | 0.67987 | 0.9773 | 1.3692 | 1.7074 | 2.0139 | 2.3291 | 2.7308 | 2.9173 | 3.1042 | 3.2924 | 3.4758 | 3.6383 | 3.7944 | 3.9391 | 4.0397 | 4.1025 | 4.1451 | 4.1602 | 4.1694 | 4.1727 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other GHG emissions (CO2e) i.e. not associated with losses |  | £m | 0 | 9.9133e-06 | 2.2496e-05 | 3.5517e-05 | 4.8478e-05 | 0.00010561 | 0.00017815 | 0.00027047 | 0.00038436 | 0.00048522 | 0.0005948 | 0.00071306 | 0.00083795 | 0.00096397 | 0.0010939 | 0.0012052 | 0.0013338 | 0.0014568 | 0.0015754 | 0.0016865 | 0.0017966 | 0.0018902 | 0.0019988 | 0.0021073 | 0.0022158 | 0.0023242 | 0.0024327 | 0.0025411 | 0.0026496 | 0.0027581 | 0.002851 | 0.0029595 | 0.003068 | 0.0031764 | 0.0032849 | 0.0034089 | 0.0035173 | 0.0036258 | 0.0037342 | 0.0038427 | 0.0039667 | 0.0040596 | 0.0041681 | 0.0042766 | 0.0043695 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fatality |  | £m | 0 | 0.0061482 | 0.012122 | 0.01729 | 0.022769 | 0.027178 | 0.031919 | 0.036489 | 0.041541 | 0.044053 | 0.046552 | 0.049034 | 0.051281 | 0.053143 | 0.054884 | 0.05637 | 0.057322 | 0.057916 | 0.058288 | 0.058382 | 0.05844 | 0.058464 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Major injury |  | £m | 0 | 0.00020881 | 0.00041175 | 0.00058733 | 0.00077342 | 0.00092314 | 0.0010841 | 0.0012394 | 0.0014109 | 0.0014962 | 0.0015811 | 0.0016654 | 0.0017417 | 0.0018049 | 0.0018641 | 0.0019145 | 0.0019469 | 0.001967 | 0.0019796 | 0.0019829 | 0.0019848 | 0.0019856 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Oil leakage |  | £m | 0 | 0.00071524 | 0.0015263 | 0.0022658 | 0.0029046 | 0.0035456 | 0.0041542 | 0.0048314 | 0.0055641 | 0.0059048 | 0.0062432 | 0.00658 | 0.0068987 | 0.0071637 | 0.007408 | 0.0076232 | 0.007765 | 0.0078564 | 0.007913 | 0.007927 | 0.0079351 | 0.0079379 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other 1 (specify) |  | £m
| Other 2 (specify) |  | £m
| Other 3 (specify) |  | £m
| Total societal net benefits |  | £m | 0 | 0.56496 | 1.0676 | 1.5345 | 2.1482 | 2.6775 | 3.1579 | 3.6519 | 4.2804 | 4.5725 | 4.865 | 5.1597 | 5.4466 | 5.7008 | 5.9449 | 6.1709 | 6.3281 | 6.4261 | 6.4928 | 6.5164 | 6.5309 | 6.536 | 6.5372 | 6.5373 | 6.5374 | 6.5375 | 6.5376 | 6.5377 | 6.5378 | 6.5379 | 6.538 | 6.5381 | 6.5382 | 6.5384 | 6.5385 | 6.5386 | 6.5387 | 6.5388 | 6.5389 | 6.539 | 6.5391 | 6.5392 | 6.5393 | 6.5395 | 6.5395 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  | £m | -0.4187 | 0.058049 | 0.48087 | 0.86815 | 1.4104 | 1.8741 | 2.2938 | 2.7341 | 3.7036 | 4.0416 | 4.3813 | 4.7244 | 5.0605 | 5.364 | 5.6578 | 5.9335 | 6.1396 | 6.2856 | 6.3994 | 6.4691 | 6.5289 | 6.5786 | 6.6238 | 6.6673 | 6.7102 | 6.7525 | 6.7942 | 6.8352 | 6.8756 | 6.9155 | 6.9546 | 6.9808 | 7.007 | 7.0332 | 7.0594 | 7.0857 | 7.1119 | 7.1381 | 7.1643 | 7.1905 | 7.2167 | 7.2428 | 7.269 | 7.2952 | 7.3214 | 0.65127 | 0.68288 | 0.71136 | 0.73665 | 0.75934 | 0.77924 | 0.79643
| Discount factor | =1/[(1+SRTP)^n] |  | 0.96618 | 0.93351 | 0.90194 | 0.87144 | 0.84197 | 0.8135 | 0.78599 | 0.75941 | 0.73373 | 0.70892 | 0.68495 | 0.66178 | 0.6394 | 0.61778 | 0.59689 | 0.57671 | 0.5572 | 0.53836 | 0.52016 | 0.50257 | 0.48557 | 0.46915 | 0.45329 | 0.43796 | 0.42315 | 0.40884 | 0.39501 | 0.38165 | 0.36875 | 0.35628 | 0.39999 | 0.38834 | 0.37703 | 0.36604 | 0.35538 | 0.34503 | 0.33498 | 0.32523 | 0.31575 | 0.30656 | 0.29763 | 0.28896 | 0.28054 | 0.27237 | 0.26444 | 0.25674 | 0.24926 | 0.242 | 0.23495 | 0.22811 | 0.22146 | 0.21501
| Discount factor (safety) | =1/[(1+PTPR)^n] |  | 0.98522 | 0.97066 | 0.95632 | 0.94218 | 0.92826 | 0.91454 | 0.90103 | 0.88771 | 0.87459 | 0.86167 | 0.84893 | 0.83639 | 0.82403 | 0.81185 | 0.79985 | 0.78803 | 0.77639 | 0.76491 | 0.75361 | 0.74247 | 0.7315 | 0.72069 | 0.71004 | 0.69954 | 0.68921 | 0.67902 | 0.66899 | 0.6591 | 0.64936 | 0.63976 | 0.63031 | 0.62099 | 0.61182 | 0.60277 | 0.59387 | 0.58509 | 0.57644 | 0.56792 | 0.55953 | 0.55126 | 0.54312 | 0.53509 | 0.52718 | 0.51939 | 0.51171 | 0.50415 | 0.4967 | 0.48936 | 0.48213 | 0.475 | 0.46798 | 0.46107
| Discounted net benefits |  | £m | -0.40454 | 0.054189 | 0.43372 | 0.75654 | 1.1875 | 1.5245 | 1.8029 | 2.0763 | 2.7175 | 2.8652 | 3.0009 | 3.1265 | 3.2357 | 3.3138 | 3.3771 | 3.4219 | 3.421 | 3.3839 | 3.3287 | 3.2511 | 3.1702 | 3.0864 | 3.0025 | 2.92 | 2.8394 | 2.7607 | 2.6838 | 2.6087 | 2.5354 | 2.4638 | 2.7818 | 2.7109 | 2.6418 | 2.5745 | 2.5088 | 2.4448 | 2.3824 | 2.3215 | 2.2621 | 2.2043 | 2.1479 | 2.0929 | 2.0393 | 1.987 | 1.9361 | 0.16721 | 0.17021 | 0.17215 | 0.17308 | 0.17321 | 0.17257 | 0.17124
| Cumulative discounted net benefits |  | £m | -0.40454 | -0.35036 | 0.083365 | 0.8399 | 2.0274 | 3.552 | 5.3549 | 7.4312 | 10.1487 | 13.0139 | 16.0148 | 19.1413 | 22.3771 | 25.6908 | 29.0679 | 32.4898 | 35.9108 | 39.2948 | 42.6235 | 45.8746 | 49.0448 | 52.1312 | 55.1337 | 58.0537 | 60.8931 | 63.6538 | 66.3376 | 68.9462 | 71.4816 | 73.9455 | 76.7272 | 79.4381 | 82.08 | 84.6545 | 87.1633 | 89.6081 | 91.9904 | 94.3119 | 96.574 | 98.7783 | 100.9262 | 103.0191 | 105.0584 | 107.0454 | 108.9815 | 109.1487 | 109.3189 | 109.491 | 109.6641 | 109.8373 | 110.0099 | 110.1811
Non-DNO (eg societal) benefits
Enter values as increments (delta) relative to your reference scenario. If this is your reference scenario enter 0. Reductions are entered as positive numbers and increases as negative numbers.
Societal net benefits (impact relative to business as usual scenario) | Reduced losses |  | MWh
| Reduced emissions associated with losses |  | tCO2e | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reduced number of customers interrupted |  | no. | 0 | 12811.1543 | 24192.6129 | 34776.3191 | 48722.5455 | 60756.5053 | 71661.4242 | 82880.8338 | 97174.5222 | 103810.7605 | 110458.7712 | 117157.4785 | 123682.2072 | 129465.9271 | 135021.9171 | 140168.5897 | 143751.0733 | 145982.7509 | 147500.4973 | 148038.2416 | 148366.6031 | 148480.7789 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125
| Reduced customer minutes lost |  | Mins | 0 | 955807.4689 | 1804949.8908 | 2594569.3331 | 3635058.353 | 4532879.4606 | 5346461.7718 | 6183501.7055 | 7249909.4558 | 7745019.1986 | 8241006.9364 | 8740776.9254 | 9227566.8639 | 9659072.3566 | 10073587.1872 | 10457564.0605 | 10724841.7943 | 10891340.2695 | 11004574.7121 | 11044694.3181 | 11069192.4046 | 11077710.7152 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147
| Reduced emissions (not associated with losses)1 |  | tCO2e | 0 | 1.2924 | 2.758 | 4.094 | 5.2482 | 6.4062 | 7.5055 | 8.729 | 10.0527 | 10.6681 | 11.2795 | 11.888 | 12.4638 | 12.9426 | 13.3838 | 13.7727 | 14.0289 | 14.194 | 14.2962 | 14.3215 | 14.3361 | 14.3412 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422
| Reduced probability of fatality2 |  | % | 0 | 0.00343 | 0.006763 | 0.0096461 | 0.012703 | 0.015162 | 0.017807 | 0.020357 | 0.023175 | 0.024576 | 0.025971 | 0.027356 | 0.028609 | 0.029648 | 0.030619 | 0.031448 | 0.031979 | 0.032311 | 0.032518 | 0.032571 | 0.032603 | 0.032617 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621
| Reduced probability of major injury2 |  | % | 0 | 0.0075965 | 0.014979 | 0.021367 | 0.028137 | 0.033584 | 0.039441 | 0.045088 | 0.051329 | 0.054433 | 0.057521 | 0.060587 | 0.063364 | 0.065664 | 0.067814 | 0.06965 | 0.070826 | 0.07156 | 0.072019 | 0.072136 | 0.072207 | 0.072237 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247
| Reduced oil leakage |  | Litres | 0 | 19.8229 | 42.302 | 62.7968 | 80.5022 | 98.268 | 115.1332 | 133.902 | 154.2097 | 163.6508 | 173.0301 | 182.3649 | 191.1978 | 198.5436 | 205.3122 | 211.2784 | 215.2088 | 217.7416 | 219.3094 | 219.6974 | 219.9215 | 219.9985 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149
1 | Includes all GHG not associated with losses e.g. SF6 converted to tCO2e using Defra conversion factors
http://www.defra.gov.uk/publications/2012/05/30/pb13773-2012-ghg-conversion/
Where losses are entered in terms of MWh, the CO2e associated with those losses will be calculated based on an assumed GHG conversion factor. The tCO2e are monetised using DECC traded carbon values.
All other GHG emissions not associated with losses should be entered in row 90 to avoid double counting.
2 | http://www.hse.gov.uk/risk/theory/alarpcheck.htm
Please specify
Total investment
Connections
Diversions
Reinforcement
ESQCR
Asset Replacement
Refurbishment
Civil Works
Operational IT & Telecoms
Legal & Safety
QoS
High Value Projects
Flooding
BT21CN
Technical losses and other environmental
High impact Low Probability (HILP)
Critical National Infrastructure
Black Start
Rising Mains and Laterals
Undergrounding Within/ Outside designated areas
Worst Served Customers
Trouble Call / faults
ONIs
Inspections & Maintenance
Tree Cutting
NOC's Other
Network Design & Engineering
Project Management
Engineering Mgt & Clerical Support
System Mapping - Cartographical
Control Centre
Call Centre
Stores
Operational Training
Vehicles & Transport
Atypicals Non Sev Weather
Smart Meters
Network Policy
HR & Non-operational Training
Finance & Regulation
CEO
IT & Telecoms
Property Mgt
Non Op Capex

## Workings 1
Workings / assumptions used for costing option 1
Use this sheet to provide details of assumptions and calculation methodology used in CBA model
Investment | Asset Replacement | Forecast cost of asset replacement programme
Please specify
Please specify
Please specify
Please specify
Total investment
Avoided DNO costs | Trouble Call / faults | Forecast reduction in repair costs following intervention. Forecast reduction estimated using probability of failure (for new assets) from CBRM asset health/ consequence models.
Please specify
Please specify
Please specify
Please specify
Please specify
Societal costs | Reduced losses
Reduced emissions associated with losses
| Reduced number of customers interrupted | Forecast reduction in customers interrupted following intervention. Forecast reduction estimated using probability of failure (for new assets) from CBRM asset health/ consequence models.
| Reduced customer minutes lost | Forecast reduction in customer minutes lost following intervention. Forecast reduction estimated using probability of failure (for new assets) from CBRM asset health/ consequence models.
| Reduced emissions (not associated with losses)1 | Forecast reduction in SF6 emissions following intervention. Forecast reduction estimated using probability of failure and consequences (for new assets) from CBRM asset health/ consequence models.
| Reduced probability of fatality2 | Forecast reduction in probability of fatality following intervention. Forecast reduction estimated using probability of failure (for new assets) from CBRM asset health/ consequence models.
| Reduced probability of major injury2 | Forecast reduction probability of major injury following intervention. Forecast reduction estimated using probability of failure (for new assets) from CBRM asset health/ consequence models.
| Reduced oil leakage | Forecast reduction in oil leakage following intervention. Forecast reduction estimated using probability of failure and consequences (for new assets) from CBRM asset health/ consequence models.

## Option 1(i)
| CBA Option 1 -Sensitivity Analysis 1(i) | Sensitivity Analysis of Option 1 - Asset Replacement Programme Delivered With 10% Increased Costs
| Term (years from first out flow) | NPV (£m)
| 16 | 31.5902
| 24 | 56.9002
| 32 | 78.117
| 45 | 107.4918
| first year of investment out flow | 1
|  |  |  | RIIO-ED1 | [7 empty] | RIIO-ED2 | [7 empty] | RIIO-ED3 | [7 empty] | RIIO-ED4 | [7 empty] | RIIO-ED5 | [7 empty] | RIIO-ED6 | [7 empty] | RIIO-ED7
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52
|  | Calculation | Units | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067
Investment | Asset Replacement |  | £m | RIIO-ED1 1: -2.1; RIIO-ED1 2: -2.0777; RIIO-ED1 3: -2.0551; RIIO-ED1 4: -2.0582; RIIO-ED1 5: -2.035; RIIO-ED1 6: -2.0123; RIIO-ED1 7: -1.9902; RIIO-ED1 8: -1.9675
| Please specify |  | £m | bar: RIIO-ED1 1 to RIIO-ED6 45
| Please specify |  | £m | bar: RIIO-ED1 1 to RIIO-ED6 45
| Please specify |  | £m | bar: RIIO-ED1 1 to RIIO-ED6 45
| Please specify |  | £m | bar: RIIO-ED1 1 to RIIO-ED6 45
| Total investment |  | £m | -2.1 | -2.0777 | -2.0551 | -2.0582 | -2.035 | -2.0123 | -1.9902 | -1.9675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avoided DNO costs | Trouble Call / faults |  | £m | 0 | 0.064888 | 0.1387 | 0.20502 | 0.26256 | 0.31995 | 0.37437 | 0.43494 | 0.50111 | 0.53166 | 0.56202 | 0.59224 | 0.62085 | 0.64466 | 0.66663 | 0.686 | 0.69879 | 0.70706 | 0.7122 | 0.71345 | 0.71418 | 0.71442 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448
| Please specify |  | £m
| Please specify |  | £m
| Please specify |  | £m
| Please specify |  | £m
| Please specify |  | £m
| Total avoided DNO costs |  | £m | 0 | 0.064888 | 0.1387 | 0.20502 | 0.26256 | 0.31995 | 0.37437 | 0.43494 | 0.50111 | 0.53166 | 0.56202 | 0.59224 | 0.62085 | 0.64466 | 0.66663 | 0.686 | 0.69879 | 0.70706 | 0.7122 | 0.71345 | 0.71418 | 0.71442 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total DNO net benefits before capitalisation | (1) = investment + DNO benefits | £m | -2.1 | -2.0128 | -1.9164 | -1.8532 | -1.7724 | -1.6924 | -1.6159 | -1.5325 | 0.50111 | 0.53166 | 0.56202 | 0.59224 | 0.62085 | 0.64466 | 0.66663 | 0.686 | 0.69879 | 0.70706 | 0.7122 | 0.71345 | 0.71418 | 0.71442 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capitalisation rates | (2) | % | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80%
| Capitalised investment | (3)=(1)x(2) | £m | -1.68 | -1.6102 | -1.5331 | -1.4825 | -1.418 | -1.3539 | -1.2927 | -1.226 | 0.40089 | 0.42533 | 0.44962 | 0.47379 | 0.49668 | 0.51573 | 0.5333 | 0.5488 | 0.55903 | 0.56565 | 0.56976 | 0.57076 | 0.57134 | 0.57154 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158
| Investment to be expensed | (4)=(1)-(3) | £m | -0.42 | -0.40256 | -0.38329 | -0.37064 | -0.35449 | -0.33848 | -0.32317 | -0.3065 | 0.10022 | 0.10633 | 0.1124 | 0.11845 | 0.12417 | 0.12893 | 0.13333 | 0.1372 | 0.13976 | 0.14141 | 0.14244 | 0.14269 | 0.14284 | 0.14288 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429
| 2016 Depreciation | (5)2016=(3)2016*Dep_ratet | £m |  | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334 | -0.037334
| 2017 Depreciation | (5)2017=(3)2017*Dep_ratet | £m |  |  | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783 | -0.035783
| 2018 Depreciation | (5)2018=(3)2018*Dep_ratet | £m |  |  |  | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407 | -0.03407
| 2019 Depreciation | (5)2019=(3)2019*Dep_ratet | £m |  |  |  |  | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946 | -0.032946
| 2020 Depreciation | (5)2020=(3)2020*Dep_ratet | £m | [5 empty] | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151 | -0.03151
| 2021 Depreciation | (5)2021=(3)2021*Dep_ratet | £m | [6 empty] | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087 | -0.030087
| 2022 Depreciation | (5)2022=(3)2022*Dep_ratet | £m | [7 empty] | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726 | -0.028726
| 2023 Depreciation | (5)2023=(3)2023*Dep_ratet | £m | [8 empty] | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245 | -0.027245
| 2024 Depreciation | (5)2024=(3)2024*Dep_ratet | £m | [9 empty] | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086
| 2025 Depreciation | (5)2025=(3)2025*Dep_ratet | £m | [10 empty] | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518
| 2026 Depreciation | (5)2026=(3)2026*Dep_ratet | £m | [11 empty] | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915
| 2027 Depreciation | (5)2027=(3)2027*Dep_ratet | £m | [12 empty] | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529
| 2028 Depreciation | (5)2028=(3)2028*Dep_ratet | £m | [13 empty] | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037
| 2029 Depreciation | (5)2029=(3)2029*Dep_ratet | £m | [14 empty] | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461
| 2030 Depreciation | (5)2030=(3)2030*Dep_ratet | £m | [15 empty] | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851
| 2031 Depreciation | (5)2031=(3)2031*Dep_ratet | £m | [16 empty] | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196
| 2032 Depreciation | (5)2032=(3)2032*Dep_ratet | £m | [17 empty] | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423
| 2033 Depreciation | (5)2033=(3)2033*Dep_ratet | £m | [18 empty] | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257
| 2034 Depreciation | (5)2034=(3)2034*Dep_ratet | £m | [19 empty] | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661
| 2035 Depreciation | (5)2035=(3)2035*Dep_ratet | £m | [20 empty] | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684
| 2036 Depreciation | (5)2036=(3)2036*Dep_ratet | £m | RIIO-ED3 22: 0.012696; RIIO-ED3 23: 0.012696; RIIO-ED3 24: 0.012696; RIIO-ED4 25: 0.012696; RIIO-ED4 26: 0.012696; RIIO-ED4 27: 0.012696; RIIO-ED4 28: 0.012696; RIIO-ED4 29: 0.012696; RIIO-ED4 30: 0.012696; RIIO-ED4 31: 0.012696; RIIO-ED4 32: 0.012696; RIIO-ED5 33: 0.012696; RIIO-ED5 34: 0.012696; RIIO-ED5 35: 0.012696; RIIO-ED5 36: 0.012696; RIIO-ED5 37: 0.012696; RIIO-ED5 38: 0.012696; RIIO-ED5 39: 0.012696; RIIO-ED5 40: 0.012696; RIIO-ED6 41: 0.012696; RIIO-ED6 42: 0.012696; RIIO-ED6 43: 0.012696; RIIO-ED6 44: 0.012696; RIIO-ED6 45: 0.012696; RIIO-ED6 46: 0.012696; RIIO-ED6 47: 0.012696; RIIO-ED6 48: 0.012696; RIIO-ED7 49: 0.012696; RIIO-ED7 50: 0.012696; RIIO-ED7 51: 0.012696; RIIO-ED7 52: 0.012696
| 2037 Depreciation | (5)2037=(3)2037*Dep_ratet | £m | RIIO-ED3 23: 0.012701; RIIO-ED3 24: 0.012701; RIIO-ED4 25: 0.012701; RIIO-ED4 26: 0.012701; RIIO-ED4 27: 0.012701; RIIO-ED4 28: 0.012701; RIIO-ED4 29: 0.012701; RIIO-ED4 30: 0.012701; RIIO-ED4 31: 0.012701; RIIO-ED4 32: 0.012701; RIIO-ED5 33: 0.012701; RIIO-ED5 34: 0.012701; RIIO-ED5 35: 0.012701; RIIO-ED5 36: 0.012701; RIIO-ED5 37: 0.012701; RIIO-ED5 38: 0.012701; RIIO-ED5 39: 0.012701; RIIO-ED5 40: 0.012701; RIIO-ED6 41: 0.012701; RIIO-ED6 42: 0.012701; RIIO-ED6 43: 0.012701; RIIO-ED6 44: 0.012701; RIIO-ED6 45: 0.012701; RIIO-ED6 46: 0.012701; RIIO-ED6 47: 0.012701; RIIO-ED6 48: 0.012701; RIIO-ED7 49: 0.012701; RIIO-ED7 50: 0.012701; RIIO-ED7 51: 0.012701; RIIO-ED7 52: 0.012701
| 2038 Depreciation | (5)2038=(3)2038*Dep_ratet | £m | RIIO-ED3 24: 0.012702; RIIO-ED4 25: 0.012702; RIIO-ED4 26: 0.012702; RIIO-ED4 27: 0.012702; RIIO-ED4 28: 0.012702; RIIO-ED4 29: 0.012702; RIIO-ED4 30: 0.012702; RIIO-ED4 31: 0.012702; RIIO-ED4 32: 0.012702; RIIO-ED5 33: 0.012702; RIIO-ED5 34: 0.012702; RIIO-ED5 35: 0.012702; RIIO-ED5 36: 0.012702; RIIO-ED5 37: 0.012702; RIIO-ED5 38: 0.012702; RIIO-ED5 39: 0.012702; RIIO-ED5 40: 0.012702; RIIO-ED6 41: 0.012702; RIIO-ED6 42: 0.012702; RIIO-ED6 43: 0.012702; RIIO-ED6 44: 0.012702; RIIO-ED6 45: 0.012702; RIIO-ED6 46: 0.012702; RIIO-ED6 47: 0.012702; RIIO-ED6 48: 0.012702; RIIO-ED7 49: 0.012702; RIIO-ED7 50: 0.012702; RIIO-ED7 51: 0.012702; RIIO-ED7 52: 0.012702
| 2039 Depreciation | (5)2039=(3)2039*Dep_ratet | £m | RIIO-ED4 25: 0.012702; RIIO-ED4 26: 0.012702; RIIO-ED4 27: 0.012702; RIIO-ED4 28: 0.012702; RIIO-ED4 29: 0.012702; RIIO-ED4 30: 0.012702; RIIO-ED4 31: 0.012702; RIIO-ED4 32: 0.012702; RIIO-ED5 33: 0.012702; RIIO-ED5 34: 0.012702; RIIO-ED5 35: 0.012702; RIIO-ED5 36: 0.012702; RIIO-ED5 37: 0.012702; RIIO-ED5 38: 0.012702; RIIO-ED5 39: 0.012702; RIIO-ED5 40: 0.012702; RIIO-ED6 41: 0.012702; RIIO-ED6 42: 0.012702; RIIO-ED6 43: 0.012702; RIIO-ED6 44: 0.012702; RIIO-ED6 45: 0.012702; RIIO-ED6 46: 0.012702; RIIO-ED6 47: 0.012702; RIIO-ED6 48: 0.012702; RIIO-ED7 49: 0.012702; RIIO-ED7 50: 0.012702; RIIO-ED7 51: 0.012702; RIIO-ED7 52: 0.012702
| 2040 Depreciation | (5)2040=(3)2040*Dep_ratet | £m | RIIO-ED4 26: 0.012702; RIIO-ED4 27: 0.012702; RIIO-ED4 28: 0.012702; RIIO-ED4 29: 0.012702; RIIO-ED4 30: 0.012702; RIIO-ED4 31: 0.012702; RIIO-ED4 32: 0.012702; RIIO-ED5 33: 0.012702; RIIO-ED5 34: 0.012702; RIIO-ED5 35: 0.012702; RIIO-ED5 36: 0.012702; RIIO-ED5 37: 0.012702; RIIO-ED5 38: 0.012702; RIIO-ED5 39: 0.012702; RIIO-ED5 40: 0.012702; RIIO-ED6 41: 0.012702; RIIO-ED6 42: 0.012702; RIIO-ED6 43: 0.012702; RIIO-ED6 44: 0.012702; RIIO-ED6 45: 0.012702; RIIO-ED6 46: 0.012702; RIIO-ED6 47: 0.012702; RIIO-ED6 48: 0.012702; RIIO-ED7 49: 0.012702; RIIO-ED7 50: 0.012702; RIIO-ED7 51: 0.012702; RIIO-ED7 52: 0.012702
| 2041 Depreciation | (5)2041=(3)2041*Dep_ratet | £m | RIIO-ED4 27: 0.012702; RIIO-ED4 28: 0.012702; RIIO-ED4 29: 0.012702; RIIO-ED4 30: 0.012702; RIIO-ED4 31: 0.012702; RIIO-ED4 32: 0.012702; RIIO-ED5 33: 0.012702; RIIO-ED5 34: 0.012702; RIIO-ED5 35: 0.012702; RIIO-ED5 36: 0.012702; RIIO-ED5 37: 0.012702; RIIO-ED5 38: 0.012702; RIIO-ED5 39: 0.012702; RIIO-ED5 40: 0.012702; RIIO-ED6 41: 0.012702; RIIO-ED6 42: 0.012702; RIIO-ED6 43: 0.012702; RIIO-ED6 44: 0.012702; RIIO-ED6 45: 0.012702; RIIO-ED6 46: 0.012702; RIIO-ED6 47: 0.012702; RIIO-ED6 48: 0.012702; RIIO-ED7 49: 0.012702; RIIO-ED7 50: 0.012702; RIIO-ED7 51: 0.012702; RIIO-ED7 52: 0.012702
| 2042 Depreciation | (5)2042=(3)2042*Dep_ratet | £m | RIIO-ED4 28: 0.012702; RIIO-ED4 29: 0.012702; RIIO-ED4 30: 0.012702; RIIO-ED4 31: 0.012702; RIIO-ED4 32: 0.012702; RIIO-ED5 33: 0.012702; RIIO-ED5 34: 0.012702; RIIO-ED5 35: 0.012702; RIIO-ED5 36: 0.012702; RIIO-ED5 37: 0.012702; RIIO-ED5 38: 0.012702; RIIO-ED5 39: 0.012702; RIIO-ED5 40: 0.012702; RIIO-ED6 41: 0.012702; RIIO-ED6 42: 0.012702; RIIO-ED6 43: 0.012702; RIIO-ED6 44: 0.012702; RIIO-ED6 45: 0.012702; RIIO-ED6 46: 0.012702; RIIO-ED6 47: 0.012702; RIIO-ED6 48: 0.012702; RIIO-ED7 49: 0.012702; RIIO-ED7 50: 0.012702; RIIO-ED7 51: 0.012702; RIIO-ED7 52: 0.012702
| 2043 Depreciation | (5)2043=(3)2043*Dep_ratet | £m | RIIO-ED4 29: 0.012702; RIIO-ED4 30: 0.012702; RIIO-ED4 31: 0.012702; RIIO-ED4 32: 0.012702; RIIO-ED5 33: 0.012702; RIIO-ED5 34: 0.012702; RIIO-ED5 35: 0.012702; RIIO-ED5 36: 0.012702; RIIO-ED5 37: 0.012702; RIIO-ED5 38: 0.012702; RIIO-ED5 39: 0.012702; RIIO-ED5 40: 0.012702; RIIO-ED6 41: 0.012702; RIIO-ED6 42: 0.012702; RIIO-ED6 43: 0.012702; RIIO-ED6 44: 0.012702; RIIO-ED6 45: 0.012702; RIIO-ED6 46: 0.012702; RIIO-ED6 47: 0.012702; RIIO-ED6 48: 0.012702; RIIO-ED7 49: 0.012702; RIIO-ED7 50: 0.012702; RIIO-ED7 51: 0.012702; RIIO-ED7 52: 0.012702
| 2044 Depreciation | (5)2044=(3)2044*Dep_ratet | £m | RIIO-ED4 30: 0.012702; RIIO-ED4 31: 0.012702; RIIO-ED4 32: 0.012702; RIIO-ED5 33: 0.012702; RIIO-ED5 34: 0.012702; RIIO-ED5 35: 0.012702; RIIO-ED5 36: 0.012702; RIIO-ED5 37: 0.012702; RIIO-ED5 38: 0.012702; RIIO-ED5 39: 0.012702; RIIO-ED5 40: 0.012702; RIIO-ED6 41: 0.012702; RIIO-ED6 42: 0.012702; RIIO-ED6 43: 0.012702; RIIO-ED6 44: 0.012702; RIIO-ED6 45: 0.012702; RIIO-ED6 46: 0.012702; RIIO-ED6 47: 0.012702; RIIO-ED6 48: 0.012702; RIIO-ED7 49: 0.012702; RIIO-ED7 50: 0.012702; RIIO-ED7 51: 0.012702; RIIO-ED7 52: 0.012702
| 2045 Depreciation | (5)2045=(3)2045*Dep_ratet | £m | RIIO-ED4 31: 0.012702; RIIO-ED4 32: 0.012702; RIIO-ED5 33: 0.012702; RIIO-ED5 34: 0.012702; RIIO-ED5 35: 0.012702; RIIO-ED5 36: 0.012702; RIIO-ED5 37: 0.012702; RIIO-ED5 38: 0.012702; RIIO-ED5 39: 0.012702; RIIO-ED5 40: 0.012702; RIIO-ED6 41: 0.012702; RIIO-ED6 42: 0.012702; RIIO-ED6 43: 0.012702; RIIO-ED6 44: 0.012702; RIIO-ED6 45: 0.012702; RIIO-ED6 46: 0.012702; RIIO-ED6 47: 0.012702; RIIO-ED6 48: 0.012702; RIIO-ED7 49: 0.012702; RIIO-ED7 50: 0.012702; RIIO-ED7 51: 0.012702; RIIO-ED7 52: 0.012702
| Depreciation | (5)=∑(5)t | £m | 0 | -0.037334 | -0.073116 | -0.10719 | -0.14013 | -0.17164 | -0.20173 | -0.23046 | -0.2577 | -0.24879 | -0.23934 | -0.22935 | -0.21882 | -0.20778 | -0.19632 | -0.18447 | -0.17227 | -0.15985 | -0.14728 | -0.13462 | -0.12194 | -0.10924 | -0.09654 | -0.083838 | -0.071136 | -0.058434 | -0.045732 | -0.033031 | -0.020329 | -0.0076271 | 0.0050747 | 0.0050747 | 0.0050747 | 0.0050747 | 0.0050747 | 0.0050747 | 0.0050747 | 0.0050747 | 0.0050747 | 0.0050747 | 0.0050747 | 0.0050747 | 0.0050747 | 0.0050747 | 0.0050747 | 0.0050747 | 0.042408 | 0.078191 | 0.11226 | 0.14521 | 0.17672 | 0.2068
| Opening RAV balance | (6op)t=(6cl)t-1 | £m | 0 | -1.68 | -3.2529 | -4.7129 | -6.0883 | -7.3661 | -8.5484 | -9.6393 | -10.6349 | -9.9763 | -9.3022 | -8.6132 | -7.9101 | -7.1946 | -6.4711 | -5.7415 | -5.0082 | -4.2769 | -3.5514 | -2.8344 | -2.129 | -1.4357 | -0.75491 | -0.086792 | 0.56863 | 1.2113 | 1.8414 | 2.4587 | 3.0633 | 3.6552 | 4.2344 | 4.8009 | 5.3674 | 5.9339 | 6.5004 | 7.0669 | 7.6334 | 8.1999 | 8.7665 | 9.333 | 9.8995 | 10.466 | 11.0325 | 11.599 | 12.1655 | 12.732 | 12.7269 | 12.6845 | 12.6063 | 12.4941 | 12.3489 | 12.1721
| Closing RAV balance | (6cl)=(3)-(5)+(6op) | £m | -1.68 | -3.2529 | -4.7129 | -6.0883 | -7.3661 | -8.5484 | -9.6393 | -10.6349 | -9.9763 | -9.3022 | -8.6132 | -7.9101 | -7.1946 | -6.4711 | -5.7415 | -5.0082 | -4.2769 | -3.5514 | -2.8344 | -2.129 | -1.4357 | -0.75491 | -0.086792 | 0.56863 | 1.2113 | 1.8414 | 2.4587 | 3.0633 | 3.6552 | 4.2344 | 4.8009 | 5.3674 | 5.9339 | 6.5004 | 7.0669 | 7.6334 | 8.1999 | 8.7665 | 9.333 | 9.8995 | 10.466 | 11.0325 | 11.599 | 12.1655 | 12.732 | 12.7269 | 12.6845 | 12.6063 | 12.4941 | 12.3489 | 12.1721 | 11.9653
| Cost of Capital | (6)=avg[(6cl),(6op)]xWACC | £m | -0.040572 | -0.11913 | -0.19238 | -0.26085 | -0.32492 | -0.38434 | -0.43923 | -0.48962 | -0.49776 | -0.46558 | -0.43266 | -0.39904 | -0.36478 | -0.33003 | -0.29493 | -0.2596 | -0.22424 | -0.18905 | -0.15422 | -0.11986 | -0.086087 | -0.052903 | -0.020327 | 0.011636 | 0.042986 | 0.073723 | 0.10385 | 0.13336 | 0.16225 | 0.19053 | 0.2182 | 0.24557 | 0.27293 | 0.30029 | 0.32765 | 0.35501 | 0.38238 | 0.40974 | 0.4371 | 0.46446 | 0.49183 | 0.51919 | 0.54655 | 0.57391 | 0.60127 | 0.61483 | 0.61369 | 0.61077 | 0.60617 | 0.59996 | 0.59218 | 0.58292
| Total Net DNO benefits | (7)=(4)+(5)+(6) | £m | -0.46057 | -0.55902 | -0.64878 | -0.73867 | -0.81954 | -0.89445 | -0.96413 | -1.0266 | -0.65524 | -0.60804 | -0.55959 | -0.50994 | -0.45943 | -0.40888 | -0.35793 | -0.30688 | -0.25675 | -0.20749 | -0.15906 | -0.11179 | -0.065189 | -0.019259 | 0.026028 | 0.070694 | 0.11475 | 0.15818 | 0.20101 | 0.24322 | 0.28482 | 0.3258 | 0.36617 | 0.39354 | 0.4209 | 0.44826 | 0.47562 | 0.50298 | 0.53035 | 0.55771 | 0.58507 | 0.61243 | 0.6398 | 0.66716 | 0.69452 | 0.72188 | 0.74924 | 0.61991 | 0.65609 | 0.68897 | 0.71844 | 0.74516 | 0.7689 | 0.78972
Societal benefits (£m) i.e. costs avoided | Losses |  | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CO2e associated with losses |  | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer interruptions (CI) |  | £m | 0 | 0.19785 | 0.37362 | 0.53707 | 0.75245 | 0.93829 | 1.1067 | 1.28 | 1.5007 | 1.6032 | 1.7059 | 1.8093 | 1.9101 | 1.9994 | 2.0852 | 2.1647 | 2.22 | 2.2545 | 2.2779 | 2.2862 | 2.2913 | 2.2931 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer minutes lost (CML) |  | £m | 0 | 0.36003 | 0.67987 | 0.9773 | 1.3692 | 1.7074 | 2.0139 | 2.3291 | 2.7308 | 2.9173 | 3.1042 | 3.2924 | 3.4758 | 3.6383 | 3.7944 | 3.9391 | 4.0397 | 4.1025 | 4.1451 | 4.1602 | 4.1694 | 4.1727 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 4.1733 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other GHG emissions (CO2e) i.e. not associated with losses |  | £m | 0 | 9.9133e-06 | 2.2496e-05 | 3.5517e-05 | 4.8478e-05 | 0.00010561 | 0.00017815 | 0.00027047 | 0.00038436 | 0.00048522 | 0.0005948 | 0.00071306 | 0.00083795 | 0.00096397 | 0.0010939 | 0.0012052 | 0.0013338 | 0.0014568 | 0.0015754 | 0.0016865 | 0.0017966 | 0.0018902 | 0.0019988 | 0.0021073 | 0.0022158 | 0.0023242 | 0.0024327 | 0.0025411 | 0.0026496 | 0.0027581 | 0.002851 | 0.0029595 | 0.003068 | 0.0031764 | 0.0032849 | 0.0034089 | 0.0035173 | 0.0036258 | 0.0037342 | 0.0038427 | 0.0039667 | 0.0040596 | 0.0041681 | 0.0042766 | 0.0043695 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fatality |  | £m | 0 | 0.0061482 | 0.012122 | 0.01729 | 0.022769 | 0.027178 | 0.031919 | 0.036489 | 0.041541 | 0.044053 | 0.046552 | 0.049034 | 0.051281 | 0.053143 | 0.054884 | 0.05637 | 0.057322 | 0.057916 | 0.058288 | 0.058382 | 0.05844 | 0.058464 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0.058472 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Major injury |  | £m | 0 | 0.00020881 | 0.00041175 | 0.00058733 | 0.00077342 | 0.00092314 | 0.0010841 | 0.0012394 | 0.0014109 | 0.0014962 | 0.0015811 | 0.0016654 | 0.0017417 | 0.0018049 | 0.0018641 | 0.0019145 | 0.0019469 | 0.001967 | 0.0019796 | 0.0019829 | 0.0019848 | 0.0019856 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0.0019859 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Oil leakage |  | £m | 0 | 0.00071524 | 0.0015263 | 0.0022658 | 0.0029046 | 0.0035456 | 0.0041542 | 0.0048314 | 0.0055641 | 0.0059048 | 0.0062432 | 0.00658 | 0.0068987 | 0.0071637 | 0.007408 | 0.0076232 | 0.007765 | 0.0078564 | 0.007913 | 0.007927 | 0.0079351 | 0.0079379 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0.0079384 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other 1 (specify) |  | £m
| Other 2 (specify) |  | £m
| Other 3 (specify) |  | £m
| Total societal net benefits |  | £m | 0 | 0.56496 | 1.0676 | 1.5345 | 2.1482 | 2.6775 | 3.1579 | 3.6519 | 4.2804 | 4.5725 | 4.865 | 5.1597 | 5.4466 | 5.7008 | 5.9449 | 6.1709 | 6.3281 | 6.4261 | 6.4928 | 6.5164 | 6.5309 | 6.536 | 6.5372 | 6.5373 | 6.5374 | 6.5375 | 6.5376 | 6.5377 | 6.5378 | 6.5379 | 6.538 | 6.5381 | 6.5382 | 6.5384 | 6.5385 | 6.5386 | 6.5387 | 6.5388 | 6.5389 | 6.539 | 6.5391 | 6.5392 | 6.5393 | 6.5395 | 6.5395 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  | £m | -0.46057 | 0.0059348 | 0.4188 | 0.79587 | 1.3286 | 1.783 | 2.1938 | 2.6254 | 3.6252 | 3.9644 | 4.3054 | 4.6498 | 4.9872 | 5.2919 | 5.587 | 5.864 | 6.0714 | 6.2186 | 6.3337 | 6.4046 | 6.4657 | 6.5167 | 6.5632 | 6.608 | 6.6521 | 6.6957 | 6.7386 | 6.7809 | 6.8226 | 6.8637 | 6.9042 | 6.9317 | 6.9591 | 6.9866 | 7.0141 | 7.0416 | 7.069 | 7.0965 | 7.124 | 7.1515 | 7.1789 | 7.2064 | 7.2339 | 7.2613 | 7.2888 | 0.61991 | 0.65609 | 0.68897 | 0.71844 | 0.74516 | 0.7689 | 0.78972
| Discount factor | =1/[(1+SRTP)^n] |  | 0.96618 | 0.93351 | 0.90194 | 0.87144 | 0.84197 | 0.8135 | 0.78599 | 0.75941 | 0.73373 | 0.70892 | 0.68495 | 0.66178 | 0.6394 | 0.61778 | 0.59689 | 0.57671 | 0.5572 | 0.53836 | 0.52016 | 0.50257 | 0.48557 | 0.46915 | 0.45329 | 0.43796 | 0.42315 | 0.40884 | 0.39501 | 0.38165 | 0.36875 | 0.35628 | 0.39999 | 0.38834 | 0.37703 | 0.36604 | 0.35538 | 0.34503 | 0.33498 | 0.32523 | 0.31575 | 0.30656 | 0.29763 | 0.28896 | 0.28054 | 0.27237 | 0.26444 | 0.25674 | 0.24926 | 0.242 | 0.23495 | 0.22811 | 0.22146 | 0.21501
| Discount factor (safety) | =1/[(1+PTPR)^n] |  | 0.98522 | 0.97066 | 0.95632 | 0.94218 | 0.92826 | 0.91454 | 0.90103 | 0.88771 | 0.87459 | 0.86167 | 0.84893 | 0.83639 | 0.82403 | 0.81185 | 0.79985 | 0.78803 | 0.77639 | 0.76491 | 0.75361 | 0.74247 | 0.7315 | 0.72069 | 0.71004 | 0.69954 | 0.68921 | 0.67902 | 0.66899 | 0.6591 | 0.64936 | 0.63976 | 0.63031 | 0.62099 | 0.61182 | 0.60277 | 0.59387 | 0.58509 | 0.57644 | 0.56792 | 0.55953 | 0.55126 | 0.54312 | 0.53509 | 0.52718 | 0.51939 | 0.51171 | 0.50415 | 0.4967 | 0.48936 | 0.48213 | 0.475 | 0.46798 | 0.46107
| Discounted net benefits |  | £m | -0.445 | 0.0055402 | 0.37773 | 0.69356 | 1.1187 | 1.4505 | 1.7243 | 1.9937 | 2.6599 | 2.8105 | 2.949 | 3.0771 | 3.1888 | 3.2692 | 3.3348 | 3.3818 | 3.383 | 3.3479 | 3.2945 | 3.2188 | 3.1396 | 3.0573 | 2.975 | 2.894 | 2.8148 | 2.7374 | 2.6618 | 2.588 | 2.5158 | 2.4454 | 2.7616 | 2.6918 | 2.6238 | 2.5574 | 2.4927 | 2.4296 | 2.368 | 2.308 | 2.2494 | 2.1923 | 2.1367 | 2.0824 | 2.0294 | 1.9778 | 1.9274 | 0.15915 | 0.16354 | 0.16673 | 0.1688 | 0.16998 | 0.17028 | 0.1698
| Cumulative discounted net benefits |  | £m | -0.445 | -0.43946 | -0.061727 | 0.63183 | 1.7505 | 3.201 | 4.9252 | 6.919 | 9.5789 | 12.3894 | 15.3383 | 18.4155 | 21.6043 | 24.8735 | 28.2083 | 31.5902 | 34.9731 | 38.321 | 41.6155 | 44.8343 | 47.9739 | 51.0312 | 54.0062 | 56.9002 | 59.715 | 62.4525 | 65.1143 | 67.7023 | 70.2181 | 72.6635 | 75.4251 | 78.117 | 80.7407 | 83.2982 | 85.7908 | 88.2204 | 90.5884 | 92.8964 | 95.1458 | 97.3381 | 99.4748 | 101.5572 | 103.5866 | 105.5643 | 107.4918 | 107.6509 | 107.8145 | 107.9812 | 108.15 | 108.32 | 108.4903 | 108.6601
Non-DNO (eg societal) benefits
Enter values as increments (delta) relative to your reference scenario. If this is your reference scenario enter 0. Reductions are entered as positive numbers and increases as negative numbers.
Societal net benefits (impact relative to business as usual scenario) | Reduced losses |  | MWh
| Reduced emissions associated with losses |  | tCO2e | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reduced number of customers interrupted |  | no. | 0 | 12811.1543 | 24192.6129 | 34776.3191 | 48722.5455 | 60756.5053 | 71661.4242 | 82880.8338 | 97174.5222 | 103810.7605 | 110458.7712 | 117157.4785 | 123682.2072 | 129465.9271 | 135021.9171 | 140168.5897 | 143751.0733 | 145982.7509 | 147500.4973 | 148038.2416 | 148366.6031 | 148480.7789 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125 | 148505.125
| Reduced customer minutes lost |  | Mins | 0 | 955807.4689 | 1804949.8908 | 2594569.3331 | 3635058.353 | 4532879.4606 | 5346461.7718 | 6183501.7055 | 7249909.4558 | 7745019.1986 | 8241006.9364 | 8740776.9254 | 9227566.8639 | 9659072.3566 | 10073587.1872 | 10457564.0605 | 10724841.7943 | 10891340.2695 | 11004574.7121 | 11044694.3181 | 11069192.4046 | 11077710.7152 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147 | 11079527.1147
| Reduced emissions (not associated with losses)1 |  | tCO2e | 0 | 1.2924 | 2.758 | 4.094 | 5.2482 | 6.4062 | 7.5055 | 8.729 | 10.0527 | 10.6681 | 11.2795 | 11.888 | 12.4638 | 12.9426 | 13.3838 | 13.7727 | 14.0289 | 14.194 | 14.2962 | 14.3215 | 14.3361 | 14.3412 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422 | 14.3422
| Reduced probability of fatality2 |  | % | 0 | 0.00343 | 0.006763 | 0.0096461 | 0.012703 | 0.015162 | 0.017807 | 0.020357 | 0.023175 | 0.024576 | 0.025971 | 0.027356 | 0.028609 | 0.029648 | 0.030619 | 0.031448 | 0.031979 | 0.032311 | 0.032518 | 0.032571 | 0.032603 | 0.032617 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621 | 0.032621
| Reduced probability of major injury2 |  | % | 0 | 0.0075965 | 0.014979 | 0.021367 | 0.028137 | 0.033584 | 0.039441 | 0.045088 | 0.051329 | 0.054433 | 0.057521 | 0.060587 | 0.063364 | 0.065664 | 0.067814 | 0.06965 | 0.070826 | 0.07156 | 0.072019 | 0.072136 | 0.072207 | 0.072237 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247 | 0.072247
| Reduced oil leakage |  | Litres | 0 | 19.8229 | 42.302 | 62.7968 | 80.5022 | 98.268 | 115.1332 | 133.902 | 154.2097 | 163.6508 | 173.0301 | 182.3649 | 191.1978 | 198.5436 | 205.3122 | 211.2784 | 215.2088 | 217.7416 | 219.3094 | 219.6974 | 219.9215 | 219.9985 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149 | 220.0149
1 | Includes all GHG not associated with losses e.g. SF6 converted to tCO2e using Defra conversion factors
http://www.defra.gov.uk/publications/2012/05/30/pb13773-2012-ghg-conversion/
Where losses are entered in terms of MWh, the CO2e associated with those losses will be calculated based on an assumed GHG conversion factor. The tCO2e are monetised using DECC traded carbon values.
All other GHG emissions not associated with losses should be entered in row 90 to avoid double counting.
2 | http://www.hse.gov.uk/risk/theory/alarpcheck.htm
Please specify
Total investment
Connections
Diversions
Reinforcement
ESQCR
Asset Replacement
Refurbishment
Civil Works
Operational IT & Telecoms
Legal & Safety
QoS
High Value Projects
Flooding
BT21CN
Technical losses and other environmental
High impact Low Probability (HILP)
Critical National Infrastructure
Black Start
Rising Mains and Laterals
Undergrounding Within/ Outside designated areas
Worst Served Customers
Trouble Call / faults
ONIs
Inspections & Maintenance
Tree Cutting
NOC's Other
Network Design & Engineering
Project Management
Engineering Mgt & Clerical Support
System Mapping - Cartographical
Control Centre
Call Centre
Stores
Operational Training
Vehicles & Transport
Atypicals Non Sev Weather
Smart Meters
Network Policy
HR & Non-operational Training
Finance & Regulation
CEO
IT & Telecoms
Property Mgt
Non Op Capex

## Option 1(ii)
| CBA Option 1 -Sensitivity Analysis 1(ii) | Sensitivity Analysis of Option 1 - Asset Replacement Programme Achieving 20% Lower Benefits
| Term (years from first out flow) | NPV (£m)
| 16 | 24.6277
| 24 | 45.0513
| 32 | 62.3535
| 45 | 86.4958
| first year of investment out flow | 1
|  |  |  | RIIO-ED1 | [7 empty] | RIIO-ED2 | [7 empty] | RIIO-ED3 | [7 empty] | RIIO-ED4 | [7 empty] | RIIO-ED5 | [7 empty] | RIIO-ED6 | [7 empty] | RIIO-ED7
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52
|  | Calculation | Units | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067
Investment | Asset Replacement |  | £m | RIIO-ED1 1: -1.9091; RIIO-ED1 2: -1.8888; RIIO-ED1 3: -1.8683; RIIO-ED1 4: -1.8711; RIIO-ED1 5: -1.85; RIIO-ED1 6: -1.8294; RIIO-ED1 7: -1.8093; RIIO-ED1 8: -1.7886
| Please specify |  | £m | bar: RIIO-ED1 1 to RIIO-ED6 45
| Please specify |  | £m | bar: RIIO-ED1 1 to RIIO-ED6 45
| Please specify |  | £m | bar: RIIO-ED1 1 to RIIO-ED6 45
| Please specify |  | £m | bar: RIIO-ED1 1 to RIIO-ED6 45
| Total investment |  | £m | -1.9091 | -1.8888 | -1.8683 | -1.8711 | -1.85 | -1.8294 | -1.8093 | -1.7886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avoided DNO costs | Trouble Call / faults |  | £m | 0 | 0.064888 | 0.1387 | 0.20502 | 0.26256 | 0.31995 | 0.37437 | 0.43494 | 0.50111 | 0.53166 | 0.56202 | 0.59224 | 0.62085 | 0.64466 | 0.66663 | 0.686 | 0.69879 | 0.70706 | 0.7122 | 0.71345 | 0.71418 | 0.71442 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448
| Please specify |  | £m
| Please specify |  | £m
| Please specify |  | £m
| Please specify |  | £m
| Please specify |  | £m
| Total avoided DNO costs |  | £m | 0 | 0.064888 | 0.1387 | 0.20502 | 0.26256 | 0.31995 | 0.37437 | 0.43494 | 0.50111 | 0.53166 | 0.56202 | 0.59224 | 0.62085 | 0.64466 | 0.66663 | 0.686 | 0.69879 | 0.70706 | 0.7122 | 0.71345 | 0.71418 | 0.71442 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total DNO net benefits before capitalisation | (1) = investment + DNO benefits | £m | -1.9091 | -1.8239 | -1.7296 | -1.6661 | -1.5874 | -1.5094 | -1.4349 | -1.3537 | 0.50111 | 0.53166 | 0.56202 | 0.59224 | 0.62085 | 0.64466 | 0.66663 | 0.686 | 0.69879 | 0.70706 | 0.7122 | 0.71345 | 0.71418 | 0.71442 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0.71448 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capitalisation rates | (2) | % | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80%
| Capitalised investment | (3)=(1)x(2) | £m | -1.5273 | -1.4591 | -1.3837 | -1.3329 | -1.27 | -1.2076 | -1.1479 | -1.0829 | 0.40089 | 0.42533 | 0.44962 | 0.47379 | 0.49668 | 0.51573 | 0.5333 | 0.5488 | 0.55903 | 0.56565 | 0.56976 | 0.57076 | 0.57134 | 0.57154 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158 | 0.57158
| Investment to be expensed | (4)=(1)-(3) | £m | -0.38182 | -0.36478 | -0.34592 | -0.33322 | -0.31749 | -0.30189 | -0.28699 | -0.27073 | 0.10022 | 0.10633 | 0.1124 | 0.11845 | 0.12417 | 0.12893 | 0.13333 | 0.1372 | 0.13976 | 0.14141 | 0.14244 | 0.14269 | 0.14284 | 0.14288 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429 | 0.1429
| 2016 Depreciation | (5)2016=(3)2016*Dep_ratet | £m |  | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394 | -0.03394
| 2017 Depreciation | (5)2017=(3)2017*Dep_ratet | £m |  |  | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425 | -0.032425
| 2018 Depreciation | (5)2018=(3)2018*Dep_ratet | £m |  |  |  | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748 | -0.030748
| 2019 Depreciation | (5)2019=(3)2019*Dep_ratet | £m |  |  |  |  | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619 | -0.029619
| 2020 Depreciation | (5)2020=(3)2020*Dep_ratet | £m | [5 empty] | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221 | -0.028221
| 2021 Depreciation | (5)2021=(3)2021*Dep_ratet | £m | [6 empty] | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835 | -0.026835
| 2022 Depreciation | (5)2022=(3)2022*Dep_ratet | £m | [7 empty] | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551 | -0.02551
| 2023 Depreciation | (5)2023=(3)2023*Dep_ratet | £m | [8 empty] | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065 | -0.024065
| 2024 Depreciation | (5)2024=(3)2024*Dep_ratet | £m | [9 empty] | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086 | 0.0089086
| 2025 Depreciation | (5)2025=(3)2025*Dep_ratet | £m | [10 empty] | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518 | 0.0094518
| 2026 Depreciation | (5)2026=(3)2026*Dep_ratet | £m | [11 empty] | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915 | 0.0099915
| 2027 Depreciation | (5)2027=(3)2027*Dep_ratet | £m | [12 empty] | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529 | 0.010529
| 2028 Depreciation | (5)2028=(3)2028*Dep_ratet | £m | [13 empty] | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037 | 0.011037
| 2029 Depreciation | (5)2029=(3)2029*Dep_ratet | £m | [14 empty] | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461 | 0.011461
| 2030 Depreciation | (5)2030=(3)2030*Dep_ratet | £m | [15 empty] | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851 | 0.011851
| 2031 Depreciation | (5)2031=(3)2031*Dep_ratet | £m | [16 empty] | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196 | 0.012196
| 2032 Depreciation | (5)2032=(3)2032*Dep_ratet | £m | [17 empty] | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423 | 0.012423
| 2033 Depreciation | (5)2033=(3)2033*Dep_ratet | £m | [18 empty] | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257 | 0.01257
| 2034 Depreciation | (5)2034=(3)2034*Dep_ratet | £m | [19 empty] | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661 | 0.012661
| 2035 Depreciation | (5)2035=(3)2035*Dep_ratet | £m | [20 empty] | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684 | 0.012684
| 2036 Depreciation | (5)2036=(3)2036*Dep_ratet | £m | RIIO-ED3 22: 0.012696; RIIO-ED3 23: 0.012696; RIIO-ED3 24: 0.012696; RIIO-ED4 25: 0.012696; RIIO-ED4 26: 0.012696; RIIO-ED4 27: 0.012696; RIIO-ED4 28: 0.012696; RIIO-ED4 29: 0.012696; RIIO-ED4 30: 0.012696; RIIO-ED4 31: 0.012696; RIIO-ED4 32: 0.012696; RIIO-ED5 33: 0.012696; RIIO-ED5 34: 0.012696; RIIO-ED5 35: 0.012696; RIIO-ED5 36: 0.012696; RIIO-ED5 37: 0.012696; RIIO-ED5 38: 0.012696; RIIO-ED5 39: 0.012696; RIIO-ED5 40: 0.012696; RIIO-ED6 41: 0.012696; RIIO-ED6 42: 0.012696; RIIO-ED6 43: 0.012696; RIIO-ED6 44: 0.012696; RIIO-ED6 45: 0.012696; RIIO-ED6 46: 0.012696; RIIO-ED6 47: 0.012696; RIIO-ED6 48: 0.012696; RIIO-ED7 49: 0.012696; RIIO-ED7 50: 0.012696; RIIO-ED7 51: 0.012696; RIIO-ED7 52: 0.012696
| 2037 Depreciation | (5)2037=(3)2037*Dep_ratet | £m | RIIO-ED3 23: 0.012701; RIIO-ED3 24: 0.012701; RIIO-ED4 25: 0.012701; RIIO-ED4 26: 0.012701; RIIO-ED4 27: 0.012701; RIIO-ED4 28: 0.012701; RIIO-ED4 29: 0.012701; RIIO-ED4 30: 0.012701; RIIO-ED4 31: 0.012701; RIIO-ED4 32: 0.012701; RIIO-ED5 33: 0.012701; RIIO-ED5 34: 0.012701; RIIO-ED5 35: 0.012701; RIIO-ED5 36: 0.012701; RIIO-ED5 37: 0.012701; RIIO-ED5 38: 0.012701; RIIO-ED5 39: 0.012701; RIIO-ED5 40: 0.012701; RIIO-ED6 41: 0.012701; RIIO-ED6 42: 0.012701; RIIO-ED6 43: 0.012701; RIIO-ED6 44: 0.012701; RIIO-ED6 45: 0.012701; RIIO-ED6 46: 0.012701; RIIO-ED6 47: 0.012701; RIIO-ED6 48: 0.012701; RIIO-ED7 49: 0.012701; RIIO-ED7 50: 0.012701; RIIO-ED7 51: 0.012701; RIIO-ED7 52: 0.012701
| 2038 Depreciation | (5)2038=(3)2038*Dep_ratet | £m | RIIO-ED3 24: 0.012702; RIIO-ED4 25: 0.012702; RIIO-ED4 26: 0.012702; RIIO-ED4 27: 0.012702; RIIO-ED4 28: 0.012702; RIIO-ED4 29: 0.012702; RIIO-ED4 30: 0.012702; RIIO-ED4 31: 0.012702; RIIO-ED4 32: 0.012702; RIIO-ED5 33: 0.012702; RIIO-ED5 34: 0.012702; RIIO-ED5 35: 0.012702; RIIO-ED5 36: 0.012702; RIIO-ED5 37: 0.012702; RIIO-ED5 38: 0.012702; RIIO-ED5 39: 0.012702; RIIO-ED5 40: 0.012702; RIIO-ED6 41: 0.012702; RIIO-ED6 42: 0.012702; RIIO-ED6 43: 0.012702; RIIO-ED6 44: 0.012702; RIIO-ED6 45: 0.012702; RIIO-ED6 46: 0.012702; RIIO-ED6 47: 0.012702; RIIO-ED6 48: 0.012702; RIIO-ED7 49: 0.012702; RIIO-ED7 50: 0.012702; RIIO-ED7 51: 0.012702; RIIO-ED7 52: 0.012702
| 2039 Depreciation | (5)2039=(3)2039*Dep_ratet | £m | RIIO-ED4 25: 0.012702; RIIO-ED4 26: 0.012702; RIIO-ED4 27: 0.012702; RIIO-ED4 28: 0.012702; RIIO-ED4 29: 0.012702; RIIO-ED4 30: 0.012702; RIIO-ED4 31: 0.012702; RIIO-ED4 32: 0.012702; RIIO-ED5 33: 0.012702; RIIO-ED5 34: 0.012702; RIIO-ED5 35: 0.012702; RIIO-ED5 36: 0.012702; RIIO-ED5 37: 0.012702; RIIO-ED5 38: 0.012702; RIIO-ED5 39: 0.012702; RIIO-ED5 40: 0.012702; RIIO-ED6 41: 0.012702; RIIO-ED6 42: 0.012702; RIIO-ED6 43: 0.012702; RIIO-ED6 44: 0.012702; RIIO-ED6 45: 0.012702; RIIO-ED6 46: 0.012702; RIIO-ED6 47: 0.012702; RIIO-ED6 48: 0.012702; RIIO-ED7 49: 0.012702; RIIO-ED7 50: 0.012702; RIIO-ED7 51: 0.012702; RIIO-ED7 52: 0.012702
| 2040 Depreciation | (5)2040=(3)2040*Dep_ratet | £m | RIIO-ED4 26: 0.012702; RIIO-ED4 27: 0.012702; RIIO-ED4 28: 0.012702; RIIO-ED4 29: 0.012702; RIIO-ED4 30: 0.012702; RIIO-ED4 31: 0.012702; RIIO-ED4 32: 0.012702; RIIO-ED5 33: 0.012702; RIIO-ED5 34: 0.012702; RIIO-ED5 35: 0.012702; RIIO-ED5 36: 0.012702; RIIO-ED5 37: 0.012702; RIIO-ED5 38: 0.012702; RIIO-ED5 39: 0.012702; RIIO-ED5 40: 0.012702; RIIO-ED6 41: 0.012702; RIIO-ED6 42: 0.012702; RIIO-ED6 43: 0.012702; RIIO-ED6 44: 0.012702; RIIO-ED6 45: 0.012702; RIIO-ED6 46: 0.012702; RIIO-ED6 47: 0.012702; RIIO-ED6 48: 0.012702; RIIO-ED7 49: 0.012702; RIIO-ED7 50: 0.012702; RIIO-ED7 51: 0.012702; RIIO-ED7 52: 0.012702
| 2041 Depreciation | (5)2041=(3)2041*Dep_ratet | £m | RIIO-ED4 27: 0.012702; RIIO-ED4 28: 0.012702; RIIO-ED4 29: 0.012702; RIIO-ED4 30: 0.012702; RIIO-ED4 31: 0.012702; RIIO-ED4 32: 0.012702; RIIO-ED5 33: 0.012702; RIIO-ED5 34: 0.012702; RIIO-ED5 35: 0.012702; RIIO-ED5 36: 0.012702; RIIO-ED5 37: 0.012702; RIIO-ED5 38: 0.012702; RIIO-ED5 39: 0.012702; RIIO-ED5 40: 0.012702; RIIO-ED6 41: 0.012702; RIIO-ED6 42: 0.012702; RIIO-ED6 43: 0.012702; RIIO-ED6 44: 0.012702; RIIO-ED6 45: 0.012702; RIIO-ED6 46: 0.012702; RIIO-ED6 47: 0.012702; RIIO-ED6 48: 0.012702; RIIO-ED7 49: 0.012702; RIIO-ED7 50: 0.012702; RIIO-ED7 51: 0.012702; RIIO-ED7 52: 0.012702
| 2042 Depreciation | (5)2042=(3)2042*Dep_ratet | £m | RIIO-ED4 28: 0.012702; RIIO-ED4 29: 0.012702; RIIO-ED4 30: 0.012702; RIIO-ED4 31: 0.012702; RIIO-ED4 32: 0.012702; RIIO-ED5 33: 0.012702; RIIO-ED5 34: 0.012702; RIIO-ED5 35: 0.012702; RIIO-ED5 36: 0.012702; RIIO-ED5 37: 0.012702; RIIO-ED5 38: 0.012702; RIIO-ED5 39: 0.012702; RIIO-ED5 40: 0.012702; RIIO-ED6 41: 0.012702; RIIO-ED6 42: 0.012702; RIIO-ED6 43: 0.012702; RIIO-ED6 44: 0.012702; RIIO-ED6 45: 0.012702; RIIO-ED6 46: 0.012702; RIIO-ED6 47: 0.012702; RIIO-ED6 48: 0.012702; RIIO-ED7 49: 0.012702; RIIO-ED7 50: 0.012702; RIIO-ED7 51: 0.012702; RIIO-ED7 52: 0.012702
| 2043 Depreciation | (5)2043=(3)2043*Dep_ratet | £m | RIIO-ED4 29: 0.012702; RIIO-ED4 30: 0.012702; RIIO-ED4 31: 0.012702; RIIO-ED4 32: 0.012702; RIIO-ED5 33: 0.012702; RIIO-ED5 34: 0.012702; RIIO-ED5 35: 0.012702; RIIO-ED5 36: 0.012702; RIIO-ED5 37: 0.012702; RIIO-ED5 38: 0.012702; RIIO-ED5 39: 0.012702; RIIO-ED5 40: 0.012702; RIIO-ED6 41: 0.012702; RIIO-ED6 42: 0.012702; RIIO-ED6 43: 0.012702; RIIO-ED6 44: 0.012702; RIIO-ED6 45: 0.012702; RIIO-ED6 46: 0.012702; RIIO-ED6 47: 0.012702; RIIO-ED6 48: 0.012702; RIIO-ED7 49: 0.012702; RIIO-ED7 50: 0.012702; RIIO-ED7 51: 0.012702; RIIO-ED7 52: 0.012702
| 2044 Depreciation | (5)2044=(3)2044*Dep_ratet | £m | RIIO-ED4 30: 0.012702; RIIO-ED4 31: 0.012702; RIIO-ED4 32: 0.012702; RIIO-ED5 33: 0.012702; RIIO-ED5 34: 0.012702; RIIO-ED5 35: 0.012702; RIIO-ED5 36: 0.012702; RIIO-ED5 37: 0.012702; RIIO-ED5 38: 0.012702; RIIO-ED5 39: 0.012702; RIIO-ED5 40: 0.012702; RIIO-ED6 41: 0.012702; RIIO-ED6 42: 0.012702; RIIO-ED6 43: 0.012702; RIIO-ED6 44: 0.012702; RIIO-ED6 45: 0.012702; RIIO-ED6 46: 0.012702; RIIO-ED6 47: 0.012702; RIIO-ED6 48: 0.012702; RIIO-ED7 49: 0.012702; RIIO-ED7 50: 0.012702; RIIO-ED7 51: 0.012702; RIIO-ED7 52: 0.012702
| 2045 Depreciation | (5)2045=(3)2045*Dep_ratet | £m | RIIO-ED4 31: 0.012702; RIIO-ED4 32: 0.012702; RIIO-ED5 33: 0.012702; RIIO-ED5 34: 0.012702; RIIO-ED5 35: 0.012702; RIIO-ED5 36: 0.012702; RIIO-ED5 37: 0.012702; RIIO-ED5 38: 0.012702; RIIO-ED5 39: 0.012702; RIIO-ED5 40: 0.012702; RIIO-ED6 41: 0.012702; RIIO-ED6 42: 0.012702; RIIO-ED6 43: 0.012702; RIIO-ED6 44: 0.012702; RIIO-ED6 45: 0.012702; RIIO-ED6 46: 0.012702; RIIO-ED6 47: 0.012702; RIIO-ED6 48: 0.012702; RIIO-ED7 49: 0.012702; RIIO-ED7 50: 0.012702; RIIO-ED7 51: 0.012702; RIIO-ED7 52: 0.012702
| Depreciation | (5)=∑(5)t | £m | 0 | -0.03394 | -0.066365 | -0.097113 | -0.12673 | -0.15495 | -0.18179 | -0.2073 | -0.23136 | -0.22245 | -0.213 | -0.20301 | -0.19248 | -0.18145 | -0.16998 | -0.15813 | -0.14594 | -0.13351 | -0.12094 | -0.10828 | -0.0956 | -0.082903 | -0.070203 | -0.057501 | -0.044799 | -0.032097 | -0.019395 | -0.0066936 | 0.0060082 | 0.01871 | 0.031412 | 0.031412 | 0.031412 | 0.031412 | 0.031412 | 0.031412 | 0.031412 | 0.031412 | 0.031412 | 0.031412 | 0.031412 | 0.031412 | 0.031412 | 0.031412 | 0.031412 | 0.031412 | 0.065351 | 0.097776 | 0.12852 | 0.15814 | 0.18637 | 0.2132
| Opening RAV balance | (6op)t=(6cl)t-1 | £m | 0 | -1.5273 | -2.9525 | -4.2698 | -5.5055 | -6.6488 | -7.7014 | -8.6675 | -9.5431 | -8.9109 | -8.2631 | -7.6005 | -6.9237 | -6.2345 | -5.5374 | -4.8341 | -4.1271 | -3.4222 | -2.723 | -2.0323 | -1.3533 | -0.68631 | -0.031869 | 0.60991 | 1.239 | 1.8554 | 2.4591 | 3.05 | 3.6283 | 4.1939 | 4.7468 | 5.2869 | 5.8271 | 6.3673 | 6.9074 | 7.4476 | 7.9878 | 8.5279 | 9.0681 | 9.6083 | 10.1484 | 10.6886 | 11.2288 | 11.769 | 12.3091 | 12.8493 | 12.8179 | 12.7525 | 12.6548 | 12.5262 | 12.3681 | 12.1817
| Closing RAV balance | (6cl)=(3)-(5)+(6op) | £m | -1.5273 | -2.9525 | -4.2698 | -5.5055 | -6.6488 | -7.7014 | -8.6675 | -9.5431 | -8.9109 | -8.2631 | -7.6005 | -6.9237 | -6.2345 | -5.5374 | -4.8341 | -4.1271 | -3.4222 | -2.723 | -2.0323 | -1.3533 | -0.68631 | -0.031869 | 0.60991 | 1.239 | 1.8554 | 2.4591 | 3.05 | 3.6283 | 4.1939 | 4.7468 | 5.2869 | 5.8271 | 6.3673 | 6.9074 | 7.4476 | 7.9878 | 8.5279 | 9.0681 | 9.6083 | 10.1484 | 10.6886 | 11.2288 | 11.769 | 12.3091 | 12.8493 | 12.8179 | 12.7525 | 12.6548 | 12.5262 | 12.3681 | 12.1817 | 11.9685
| Cost of Capital | (6)=avg[(6cl),(6op)]xWACC | £m | -0.036884 | -0.10819 | -0.17442 | -0.23607 | -0.29353 | -0.34656 | -0.39531 | -0.43979 | -0.44566 | -0.41475 | -0.38311 | -0.35076 | -0.31777 | -0.28429 | -0.25047 | -0.21641 | -0.18232 | -0.14841 | -0.11484 | -0.081761 | -0.049255 | -0.017344 | 0.01396 | 0.044651 | 0.074729 | 0.10419 | 0.13304 | 0.16128 | 0.18891 | 0.21592 | 0.24231 | 0.2684 | 0.29449 | 0.32058 | 0.34667 | 0.37276 | 0.39885 | 0.42494 | 0.45103 | 0.47712 | 0.50321 | 0.52931 | 0.5554 | 0.58149 | 0.60758 | 0.61986 | 0.61753 | 0.61359 | 0.60812 | 0.6012 | 0.59288 | 0.58323
| Total Net DNO benefits | (7)=(4)+(5)+(6) | £m | -0.4187 | -0.50691 | -0.5867 | -0.6664 | -0.73775 | -0.8034 | -0.86408 | -0.91782 | -0.57681 | -0.53087 | -0.4837 | -0.43532 | -0.38608 | -0.3368 | -0.28713 | -0.23735 | -0.1885 | -0.14051 | -0.093345 | -0.047354 | -0.0020204 | 0.042637 | 0.086652 | 0.13005 | 0.17283 | 0.21499 | 0.25654 | 0.29748 | 0.33781 | 0.37752 | 0.41662 | 0.44271 | 0.4688 | 0.49489 | 0.52098 | 0.54707 | 0.57316 | 0.59925 | 0.62534 | 0.65143 | 0.67752 | 0.70361 | 0.7297 | 0.75579 | 0.78188 | 0.65127 | 0.68288 | 0.71136 | 0.73665 | 0.75934 | 0.77924 | 0.79643
Societal benefits (£m) i.e. costs avoided | Losses |  | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CO2e associated with losses |  | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer interruptions (CI) |  | £m | 0 | 0.15828 | 0.2989 | 0.42966 | 0.60196 | 0.75064 | 0.88536 | 1.024 | 1.2006 | 1.2826 | 1.3647 | 1.4475 | 1.5281 | 1.5995 | 1.6682 | 1.7318 | 1.776 | 1.8036 | 1.8223 | 1.829 | 1.833 | 1.8345 | 1.8348 | 1.8348 | 1.8348 | 1.8348 | 1.8348 | 1.8348 | 1.8348 | 1.8348 | 1.8348 | 1.8348 | 1.8348 | 1.8348 | 1.8348 | 1.8348 | 1.8348 | 1.8348 | 1.8348 | 1.8348 | 1.8348 | 1.8348 | 1.8348 | 1.8348 | 1.8348 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer minutes lost (CML) |  | £m | 0 | 0.28802 | 0.5439 | 0.78184 | 1.0954 | 1.3659 | 1.6111 | 1.8633 | 2.1847 | 2.3339 | 2.4833 | 2.6339 | 2.7806 | 2.9106 | 3.0355 | 3.1513 | 3.2318 | 3.282 | 3.3161 | 3.3282 | 3.3356 | 3.3381 | 3.3387 | 3.3387 | 3.3387 | 3.3387 | 3.3387 | 3.3387 | 3.3387 | 3.3387 | 3.3387 | 3.3387 | 3.3387 | 3.3387 | 3.3387 | 3.3387 | 3.3387 | 3.3387 | 3.3387 | 3.3387 | 3.3387 | 3.3387 | 3.3387 | 3.3387 | 3.3387 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other GHG emissions (CO2e) i.e. not associated with losses |  | £m | 0 | 7.9306e-06 | 1.7997e-05 | 2.8413e-05 | 3.8782e-05 | 8.4491e-05 | 0.00014252 | 0.00021637 | 0.00030749 | 0.00038818 | 0.00047584 | 0.00057045 | 0.00067036 | 0.00077117 | 0.00087508 | 0.00096419 | 0.001067 | 0.0011654 | 0.0012603 | 0.0013492 | 0.0014373 | 0.0015122 | 0.0015991 | 0.0016858 | 0.0017726 | 0.0018594 | 0.0019461 | 0.0020329 | 0.0021197 | 0.0022065 | 0.0022808 | 0.0023676 | 0.0024544 | 0.0025411 | 0.0026279 | 0.0027271 | 0.0028139 | 0.0029006 | 0.0029874 | 0.0030742 | 0.0031733 | 0.0032477 | 0.0033345 | 0.0034213 | 0.0034956 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fatality |  | £m | 0 | 0.0049185 | 0.0096979 | 0.013832 | 0.018216 | 0.021742 | 0.025535 | 0.029191 | 0.033233 | 0.035242 | 0.037242 | 0.039228 | 0.041025 | 0.042514 | 0.043907 | 0.045096 | 0.045857 | 0.046333 | 0.04663 | 0.046706 | 0.046752 | 0.046772 | 0.046778 | 0.046778 | 0.046778 | 0.046778 | 0.046778 | 0.046778 | 0.046778 | 0.046778 | 0.046778 | 0.046778 | 0.046778 | 0.046778 | 0.046778 | 0.046778 | 0.046778 | 0.046778 | 0.046778 | 0.046778 | 0.046778 | 0.046778 | 0.046778 | 0.046778 | 0.046778 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Major injury |  | £m | 0 | 0.00016705 | 0.0003294 | 0.00046986 | 0.00061873 | 0.00073851 | 0.00086731 | 0.0009915 | 0.0011287 | 0.001197 | 0.0012649 | 0.0013323 | 0.0013934 | 0.001444 | 0.0014912 | 0.0015316 | 0.0015575 | 0.0015736 | 0.0015837 | 0.0015863 | 0.0015879 | 0.0015885 | 0.0015887 | 0.0015887 | 0.0015887 | 0.0015887 | 0.0015887 | 0.0015887 | 0.0015887 | 0.0015887 | 0.0015887 | 0.0015887 | 0.0015887 | 0.0015887 | 0.0015887 | 0.0015887 | 0.0015887 | 0.0015887 | 0.0015887 | 0.0015887 | 0.0015887 | 0.0015887 | 0.0015887 | 0.0015887 | 0.0015887 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Oil leakage |  | £m | 0 | 0.00057219 | 0.0012211 | 0.0018126 | 0.0023237 | 0.0028365 | 0.0033233 | 0.0038651 | 0.0044513 | 0.0047238 | 0.0049945 | 0.005264 | 0.005519 | 0.005731 | 0.0059264 | 0.0060986 | 0.006212 | 0.0062851 | 0.0063304 | 0.0063416 | 0.0063481 | 0.0063503 | 0.0063508 | 0.0063508 | 0.0063508 | 0.0063508 | 0.0063508 | 0.0063508 | 0.0063508 | 0.0063508 | 0.0063508 | 0.0063508 | 0.0063508 | 0.0063508 | 0.0063508 | 0.0063508 | 0.0063508 | 0.0063508 | 0.0063508 | 0.0063508 | 0.0063508 | 0.0063508 | 0.0063508 | 0.0063508 | 0.0063508 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other 1 (specify) |  | £m
| Other 2 (specify) |  | £m
| Other 3 (specify) |  | £m
| Total societal net benefits |  | £m | 0 | 0.45197 | 0.85406 | 1.2276 | 1.7185 | 2.142 | 2.5263 | 2.9216 | 3.4244 | 3.658 | 3.892 | 4.1278 | 4.3573 | 4.5606 | 4.7559 | 4.9367 | 5.0625 | 5.1409 | 5.1942 | 5.2131 | 5.2247 | 5.2288 | 5.2297 | 5.2298 | 5.2299 | 5.23 | 5.2301 | 5.2302 | 5.2303 | 5.2303 | 5.2304 | 5.2305 | 5.2306 | 5.2307 | 5.2308 | 5.2309 | 5.231 | 5.231 | 5.2311 | 5.2312 | 5.2313 | 5.2314 | 5.2315 | 5.2316 | 5.2316 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net benefits |  | £m | -0.4187 | -0.054943 | 0.26736 | 0.56124 | 0.98079 | 1.3386 | 1.6622 | 2.0037 | 2.8476 | 3.1271 | 3.4083 | 3.6925 | 3.9712 | 4.2238 | 4.4688 | 4.6994 | 4.874 | 5.0004 | 5.1009 | 5.1658 | 5.2227 | 5.2714 | 5.3164 | 5.3599 | 5.4027 | 5.445 | 5.4866 | 5.5277 | 5.5681 | 5.6079 | 5.647 | 5.6732 | 5.6994 | 5.7256 | 5.7518 | 5.7779 | 5.8041 | 5.8303 | 5.8565 | 5.8826 | 5.9088 | 5.935 | 5.9612 | 5.9874 | 6.0135 | 0.65127 | 0.68288 | 0.71136 | 0.73665 | 0.75934 | 0.77924 | 0.79643
| Discount factor | =1/[(1+SRTP)^n] |  | 0.96618 | 0.93351 | 0.90194 | 0.87144 | 0.84197 | 0.8135 | 0.78599 | 0.75941 | 0.73373 | 0.70892 | 0.68495 | 0.66178 | 0.6394 | 0.61778 | 0.59689 | 0.57671 | 0.5572 | 0.53836 | 0.52016 | 0.50257 | 0.48557 | 0.46915 | 0.45329 | 0.43796 | 0.42315 | 0.40884 | 0.39501 | 0.38165 | 0.36875 | 0.35628 | 0.39999 | 0.38834 | 0.37703 | 0.36604 | 0.35538 | 0.34503 | 0.33498 | 0.32523 | 0.31575 | 0.30656 | 0.29763 | 0.28896 | 0.28054 | 0.27237 | 0.26444 | 0.25674 | 0.24926 | 0.242 | 0.23495 | 0.22811 | 0.22146 | 0.21501
| Discount factor (safety) | =1/[(1+PTPR)^n] |  | 0.98522 | 0.97066 | 0.95632 | 0.94218 | 0.92826 | 0.91454 | 0.90103 | 0.88771 | 0.87459 | 0.86167 | 0.84893 | 0.83639 | 0.82403 | 0.81185 | 0.79985 | 0.78803 | 0.77639 | 0.76491 | 0.75361 | 0.74247 | 0.7315 | 0.72069 | 0.71004 | 0.69954 | 0.68921 | 0.67902 | 0.66899 | 0.6591 | 0.64936 | 0.63976 | 0.63031 | 0.62099 | 0.61182 | 0.60277 | 0.59387 | 0.58509 | 0.57644 | 0.56792 | 0.55953 | 0.55126 | 0.54312 | 0.53509 | 0.52718 | 0.51939 | 0.51171 | 0.50415 | 0.4967 | 0.48936 | 0.48213 | 0.475 | 0.46798 | 0.46107
| Discounted net benefits |  | £m | -0.40454 | -0.05129 | 0.24114 | 0.48908 | 0.8258 | 1.0889 | 1.3065 | 1.5217 | 2.0893 | 2.2169 | 2.3345 | 2.4436 | 2.5392 | 2.6094 | 2.6674 | 2.7101 | 2.7158 | 2.692 | 2.6533 | 2.5961 | 2.536 | 2.4731 | 2.4098 | 2.3474 | 2.2862 | 2.2261 | 2.1673 | 2.1097 | 2.0532 | 1.998 | 2.2587 | 2.2031 | 2.1488 | 2.0958 | 2.0441 | 1.9936 | 1.9443 | 1.8962 | 1.8492 | 1.8034 | 1.7586 | 1.715 | 1.6724 | 1.6308 | 1.5902 | 0.16721 | 0.17021 | 0.17215 | 0.17308 | 0.17321 | 0.17257 | 0.17124
| Cumulative discounted net benefits |  | £m | -0.40454 | -0.45583 | -0.21469 | 0.27439 | 1.1002 | 2.1891 | 3.4956 | 5.0173 | 7.1066 | 9.3235 | 11.658 | 14.1016 | 16.6408 | 19.2502 | 21.9176 | 24.6277 | 27.3435 | 30.0355 | 32.6888 | 35.2849 | 37.8209 | 40.294 | 42.7039 | 45.0513 | 47.3374 | 49.5635 | 51.7308 | 53.8405 | 55.8937 | 57.8917 | 60.1504 | 62.3535 | 64.5024 | 66.5982 | 68.6422 | 70.6358 | 72.5801 | 74.4763 | 76.3255 | 78.1288 | 79.8875 | 81.6024 | 83.2748 | 84.9056 | 86.4958 | 86.663 | 86.8332 | 87.0054 | 87.1784 | 87.3517 | 87.5242 | 87.6955
Non-DNO (eg societal) benefits
Enter values as increments (delta) relative to your reference scenario. If this is your reference scenario enter 0. Reductions are entered as positive numbers and increases as negative numbers.
Societal net benefits (impact relative to business as usual scenario) | Reduced losses |  | MWh
| Reduced emissions associated with losses |  | tCO2e | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reduced number of customers interrupted |  | no. | 0 | 10248.9234 | 19354.0903 | 27821.0553 | 38978.0364 | 48605.2042 | 57329.1393 | 66304.667 | 77739.6178 | 83048.6084 | 88367.017 | 93725.9828 | 98945.7657 | 103572.7417 | 108017.5336 | 112134.8718 | 115000.8587 | 116786.2007 | 118000.3978 | 118430.5933 | 118693.2825 | 118784.6231 | 118804.1 | 118804.1 | 118804.1 | 118804.1 | 118804.1 | 118804.1 | 118804.1 | 118804.1 | 118804.1 | 118804.1 | 118804.1 | 118804.1 | 118804.1 | 118804.1 | 118804.1 | 118804.1 | 118804.1 | 118804.1 | 118804.1 | 118804.1 | 118804.1 | 118804.1 | 118804.1
| Reduced customer minutes lost |  | Mins | 0 | 764645.9751 | 1443959.9126 | 2075655.4665 | 2908046.6824 | 3626303.5685 | 4277169.4175 | 4946801.3644 | 5799927.5647 | 6196015.3589 | 6592805.5491 | 6992621.5404 | 7382053.4911 | 7727257.8853 | 8058869.7497 | 8366051.2484 | 8579873.4355 | 8713072.2156 | 8803659.7697 | 8835755.4545 | 8855353.9237 | 8862168.5722 | 8863621.6918 | 8863621.6918 | 8863621.6918 | 8863621.6918 | 8863621.6918 | 8863621.6918 | 8863621.6918 | 8863621.6918 | 8863621.6918 | 8863621.6918 | 8863621.6918 | 8863621.6918 | 8863621.6918 | 8863621.6918 | 8863621.6918 | 8863621.6918 | 8863621.6918 | 8863621.6918 | 8863621.6918 | 8863621.6918 | 8863621.6918 | 8863621.6918 | 8863621.6918
| Reduced emissions (not associated with losses)1 |  | tCO2e | 0 | 1.0339 | 2.2064 | 3.2752 | 4.1985 | 5.1249 | 6.0044 | 6.9832 | 8.0422 | 8.5345 | 9.0236 | 9.5104 | 9.971 | 10.3541 | 10.7071 | 11.0182 | 11.2232 | 11.3552 | 11.437 | 11.4572 | 11.4689 | 11.4729 | 11.4738 | 11.4738 | 11.4738 | 11.4738 | 11.4738 | 11.4738 | 11.4738 | 11.4738 | 11.4738 | 11.4738 | 11.4738 | 11.4738 | 11.4738 | 11.4738 | 11.4738 | 11.4738 | 11.4738 | 11.4738 | 11.4738 | 11.4738 | 11.4738 | 11.4738 | 11.4738
| Reduced probability of fatality2 |  | % | 0 | 0.002744 | 0.0054104 | 0.0077169 | 0.010162 | 0.01213 | 0.014246 | 0.016285 | 0.01854 | 0.019661 | 0.020777 | 0.021885 | 0.022887 | 0.023718 | 0.024495 | 0.025158 | 0.025583 | 0.025849 | 0.026014 | 0.026057 | 0.026082 | 0.026093 | 0.026097 | 0.026097 | 0.026097 | 0.026097 | 0.026097 | 0.026097 | 0.026097 | 0.026097 | 0.026097 | 0.026097 | 0.026097 | 0.026097 | 0.026097 | 0.026097 | 0.026097 | 0.026097 | 0.026097 | 0.026097 | 0.026097 | 0.026097 | 0.026097 | 0.026097 | 0.026097
| Reduced probability of major injury2 |  | % | 0 | 0.0060772 | 0.011984 | 0.017093 | 0.022509 | 0.026867 | 0.031553 | 0.036071 | 0.041063 | 0.043546 | 0.046017 | 0.04847 | 0.050691 | 0.052531 | 0.054251 | 0.05572 | 0.056661 | 0.057248 | 0.057615 | 0.057709 | 0.057766 | 0.05779 | 0.057797 | 0.057797 | 0.057797 | 0.057797 | 0.057797 | 0.057797 | 0.057797 | 0.057797 | 0.057797 | 0.057797 | 0.057797 | 0.057797 | 0.057797 | 0.057797 | 0.057797 | 0.057797 | 0.057797 | 0.057797 | 0.057797 | 0.057797 | 0.057797 | 0.057797 | 0.057797
| Reduced oil leakage |  | Litres | 0 | 15.8583 | 33.8416 | 50.2374 | 64.4018 | 78.6144 | 92.1066 | 107.1216 | 123.3677 | 130.9206 | 138.4241 | 145.8919 | 152.9583 | 158.8349 | 164.2498 | 169.0227 | 172.167 | 174.1933 | 175.4475 | 175.7579 | 175.9372 | 175.9988 | 176.0119 | 176.0119 | 176.0119 | 176.0119 | 176.0119 | 176.0119 | 176.0119 | 176.0119 | 176.0119 | 176.0119 | 176.0119 | 176.0119 | 176.0119 | 176.0119 | 176.0119 | 176.0119 | 176.0119 | 176.0119 | 176.0119 | 176.0119 | 176.0119 | 176.0119 | 176.0119
1 | Includes all GHG not associated with losses e.g. SF6 converted to tCO2e using Defra conversion factors
http://www.defra.gov.uk/publications/2012/05/30/pb13773-2012-ghg-conversion/
Where losses are entered in terms of MWh, the CO2e associated with those losses will be calculated based on an assumed GHG conversion factor. The tCO2e are monetised using DECC traded carbon values.
All other GHG emissions not associated with losses should be entered in row 90 to avoid double counting.
2 | http://www.hse.gov.uk/risk/theory/alarpcheck.htm
Please specify
Total investment
Connections
Diversions
Reinforcement
ESQCR
Asset Replacement
Refurbishment
Civil Works
Operational IT & Telecoms
Legal & Safety
QoS
High Value Projects
Flooding
BT21CN
Technical losses and other environmental
High impact Low Probability (HILP)
Critical National Infrastructure
Black Start
Rising Mains and Laterals
Undergrounding Within/ Outside designated areas
Worst Served Customers
Trouble Call / faults
ONIs
Inspections & Maintenance
Tree Cutting
NOC's Other
Network Design & Engineering
Project Management
Engineering Mgt & Clerical Support
System Mapping - Cartographical
Control Centre
Call Centre
Stores
Operational Training
Vehicles & Transport
Atypicals Non Sev Weather
Smart Meters
Network Policy
HR & Non-operational Training
Finance & Regulation
CEO
IT & Telecoms
Property Mgt
Non Op Capex